## HT Cable
|  | 2x800 MW ULTRA SUPER CRITICAL THERMAL POWER PROJECT, RAIGARH (PHASE-II), RAIPUR, CHHATTISGARH | [36 empty] | Terminations
ATTCHMENT 2 - 11kV_HT CABLE SIZNG
SL No | Description | LOAD | [8 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  |  | CABLE DATA | [5 empty] | CURRENT CARRYING CAPACITY | [8 empty] | VOLTAGE DROP |  |  | MOTOR STARTING VOLTAGE DIP |  |  | Selected Cable Size / Phase | Total Length in meters | Remarks | Termination Kits | Joining Kits
|  | Type of feeder | Rated power |  | Rated Voltage | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard | Short circuit current withstand duration | Minimum size required for Short circuit withstand capacity | Installation | No. of Cores | Size | Current Rating of the Cable | Cable resistance at 90°C | Cable reactance at 50Hz | Cable length | DERATING FACTOR | [5 empty] | Derated current carrying capacity | No. of Runs/Phase | Derated current > Rated current | ∆U | % | Allowable | ∆U | % | Allowable | [5 empty] | AIR | 1C | 185
|  |  | kVA | kW | kV |  |  | A | A |  | kA | Sec | Sq.mm |  |  | Sq.mm | A | Ohm / Ph / km | Ohm / Ph / km | Meters | Ambient temperature (K1) | Grouping factor (K2) | Ground temprature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | A | [13 empty] | GROUND | 3C | 240
11kV SWITCHGEAR | [40 empty] | DUCT |  | 300
| 11 KV UNIT SWGR-3UA | [41 empty] | 400
1 | FD FAN-3A | M |  | 2450 | 11 | 0.85 | 0.92 | 164.4443 | 1183.9988 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 475 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 24.9015 | 0.22638 | YES | 115.5502 | 1.0505 | YES | 1R X 11kV X 3C X 240 Sqmm | 475 |  | 2 |  |  |  | 500
2 | PA Fan 3A | M |  | 3900 | 11 | 0.88 | 0.95 | 244.86 | 1762.9916 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 300 | 441 | 0.13 | 0.086 | 500 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 286.5177 | 1 | YES | 32.921 | 0.29928 | YES | 168.3482 | 1.5304 | YES | 1R X 11kV X 3C X 300 Sqmm | 500 |  | 2 |  |  |  | 630
3 | CW Pump #1 | M |  | 4325 | 11 | 0.77 | 0.945 | 311.9773 | 2246.2366 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 300 | 387 | 0.162 | 0.088 | 750 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 2 | YES | 36.6542 | 0.33322 | YES | 173.0664 | 1.5733 | YES | 2R X 11kV X 1C X 300 Sqmm | 4500 |  | 4
4 | ID FAN #3A | M |  | 11350 | 11 | 0.85 | 0.97 | 722.5445 | 5202.3207 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 300 | 575 | 0.1018 | 0.0937 | 410 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 34.863 | 0.31694 | YES | 207.1936 | 1.8836 | YES | 2R X 11kV X 1C X 300 Sqmm | 2460 |  | 4
5 | MDBFP | M |  | 13000 | 11 | 0.85 | 0.92 | 872.5615 | 6282.4425 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 85 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 3 | YES | 5.8189 | 0.052899 | YES | 34.5821 | 0.31438 | YES | 3R X 11kV X 1C X 400 Sqmm | 765 |  | 6
6 | HVAC Transformer Feeder | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 460 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 23.0914 | 0.20992 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 460 |  | 2
7 | Turbine Tower Service Transformer Feeder | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 470 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 19.6612 | 0.17874 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 470 |  | 2
8 | Boiler Service Transformer Feeder | F | 3150 |  | 11 | 0.85 | 0.92 | 165.337 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 460 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 24.246 | 0.22042 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 460 |  | 2
9 | ESP Service Transformer Feeder-1 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
10 | ESP Service Transformer Feeder-2 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
11 | ESP Service Transformer Feeder-3 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
12 | Cooling Tower Transformer Feeder-2A | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 1100 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 55.2187 | 0.50199 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 1100 |  | 2
13 | UAT Auxiliary Transformer Feeder | F | 20000 |  | 11 | 0.85 | 0.92 | 1049.7586 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 120 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 3 | YES | 9.8832 | 0.089847 | YES | NA | NA | NA | 3R X 11kV X 1C X 400 Sqmm | 1080 |  | 6
| 11 KV UNIT SWGR-3UB | [37 empty] | 0
1 | FD FAN-3B | M |  | 2450 | 11 | 0.85 | 0.92 | 164.4443 | 1183.9988 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 475 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 24.9015 | 0.22638 | YES | 115.5502 | 1.0505 | YES | 1R X 11kV X 3C X 240 Sqmm | 475 |  | 2
2 | PA Fan 3B | M |  | 3900 | 11 | 0.88 | 0.95 | 244.86 | 1762.9916 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 300 | 441 | 0.13 | 0.086 | 500 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 286.5177 | 1 | YES | 32.921 | 0.29928 | YES | 168.3482 | 1.5304 | YES | 1R X 11kV X 3C X 300 Sqmm | 500 |  | 2
3 | CW Pump #2 | M |  | 4325 | 11 | 0.77 | 0.945 | 311.9773 | 2246.2366 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 300 | 387 | 0.162 | 0.088 | 750 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 2 | YES | 36.6542 | 0.33322 | YES | 173.0664 | 1.5733 | YES | 2R X 11kV X 1C X 300 Sqmm | 4500 |  | 4
4 | ID FAN #3B | M |  | 11350 | 11 | 0.85 | 0.97 | 722.5445 | 5202.3207 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 410 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 34.863 | 0.31694 | YES | 207.1936 | 1.8836 | YES | 2R X 11kV X 1C X 400 Sqmm | 2460 |  | 4
5 | UAT Auxiliary Transformer Feeder | F | 20000 |  | 11 | 0.83 | 0.93 | 1049.7586 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 120 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 3 | YES | 9.9462 | 0.09042 | YES | NA | NA | NA | 3R X 11kV X 1C X 400 Sqmm | 1080 |  | 6
6 | HVAC Service Transformer Feeder | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 460 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 23.0914 | 0.20992 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 460
7 | Turbine Tower Service Transformer Feeder | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 470 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 19.6612 | 0.17874 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 470 |  | 2
8 | Boiler Service Transformer Feeder | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 460 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 23.0914 | 0.20992 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 460 |  | 2
9 | ESP Service Transformer Feeder-4 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
10 | ESP Service Transformer Feeder-5 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
11 | ESP Service Transformer Feeder-6 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
12 | Cooling Tower Transformer Feeder-2B | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 1100 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 55.2187 | 0.50199 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 1100 |  | 2
13
| 11 KV UNIT SWGR-4UA | [37 empty] | 0
1 | FD FAN-4A | M |  | 2450 | 11 | 0.77 | 0.945 | 176.727 | 1272.4346 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 475 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 26.3007 | 0.2391 | YES | 124.181 | 1.1289 | YES | 1R X 11kV X 3C X 240 Sqmm | 475 |  | 2
2 | PA FAN-4A | M |  | 3900 | 11 | 0.88 | 0.95 | 244.86 | 1762.9916 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 300 | 441 | 0.13 | 0.086 | 500 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 286.5177 | 1 | YES | 32.921 | 0.29928 | YES | 168.3482 | 1.5304 | YES | 1R X 11kV X 3C X 300 Sqmm | 500 |  | 2
3 | CW Pump Motor#3 | M |  | 4325 | 11 | 0.77 | 0.945 | 311.9773 | 2246.2366 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 300 | 387 | 0.162 | 0.088 | 750 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 2 | YES | 36.6542 | 0.33322 | YES | 173.0664 | 1.5733 | YES | 2R X 11kV X 1C X 300 Sqmm | 4500 |  | 4
4 | ID FAN-4A | M |  | 11350 | 11 | 0.85 | 0.97 | 722.5445 | 5202.3207 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 410 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 34.863 | 0.31694 | YES | 207.1936 | 1.8836 | YES | 2R X 11kV X 1C X 400 Sqmm | 2460 |  | 4
5 | MDBFP Motor | M |  | 13000 | 11 | 0.85 | 0.97 | 827.5841 | 5958.6053 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 85 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 3 | YES | 5.5189 | 0.050172 | YES | 32.7995 | 0.29818 | YES | 3R X 11kV X 1C X 400 Sqmm | 765 |  | 6
6 | Turbine Tower Service Transformer Feeder | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 470 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 19.6612 | 0.17874 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 470 |  | 2
7 | Boiler Service Transformer Feeder | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 470 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 23.5934 | 0.21449 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 470 |  | 2
8 | ESP Service Transformer Feeder-1 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
9 | ESP Service Transformer Feeder-2 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
10 | ESP Service Transformer Feeder-3 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
11 | HVAC Transformer Feeder | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 24.5974 | 0.22361 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
12 | Cooling Tower Transformer Feeder-3A | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 1100 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 55.2187 | 0.50199 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 1100 |  | 2
13 | UAT Auxiliary Transformer Feeder | F | 20000 |  | 11 | 0.85 | 0.92 | 1049.7586 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 120 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 3 | YES | 9.8832 | 0.089847 | YES | NA | NA | NA | 3R X 11kV X 1C X 400 Sqmm | 1080 |  | 6
| 11 KV UNIT SWGR-4UB | [37 empty] | 0
1 | FD FAN-4B | M |  | 2450 | 11 | 0.77 | 0.945 | 176.727 | 1272.4346 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 475 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 26.3007 | 0.2391 | YES | 124.181 | 1.1289 | YES | 1R X 11kV X 3C X 240 Sqmm | 475 |  | 2
2 | PA FAN-4B | M |  | 3900 | 11 | 0.88 | 0.95 | 244.86 | 1762.9916 | 0.2 | 50 | 0.16 | 212.766 | AIR | 3C | 300 | 441 | 0.13 | 0.086 | 500 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 286.5177 | 1 | YES | 32.921 | 0.29928 | YES | 168.3482 | 1.5304 | YES | 1R X 11kV X 3C X 300 Sqmm | 500 |  | 2
3 | CW Pump Motor#4 | M |  | 4325 | 11 | 0.77 | 0.945 | 311.9773 | 2246.2366 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 300 | 387 | 0.162 | 0.088 | 750 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 2 | YES | 36.6542 | 0.33322 | YES | 173.0664 | 1.5733 | YES | 2R X 11kV X 1C X 300 Sqmm | 4500 |  | 4
4 | ID FAN-4B | M |  | 11350 | 11 | 0.85 | 0.97 | 722.5445 | 5202.3207 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 410 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 34.863 | 0.31694 | YES | 207.1936 | 1.8836 | YES | 2R X 11kV X 1C X 400 Sqmm | 2460 |  | 4
5 | HVAC Service Transformer Feeder | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 470 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 23.5934 | 0.21449 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 470
6 | Turbine Tower Service Transformer Feeder | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 470 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 19.6612 | 0.17874 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 470 |  | 2
7 | Boiler Service Transformer Feeder | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 24.5974 | 0.22361 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
8 | ESP Service Transformer Feeder-4 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
9 | ESP Service Transformer Feeder-5 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
10 | ESP Service Transformer Feeder-6 | F | 2500 |  | 11 | 0.85 | 0.92 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.4978 | 0.18634 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 490 |  | 2
11 | Cooling Tower Transformer Feeder-3B | F | 3000 |  | 11 | 0.85 | 0.92 | 157.4638 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 1100 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 55.2187 | 0.50199 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 1100 |  | 2
12 | UAT Auxiliary Transformer Feeder | F | 20000 |  | 11 | 0.85 | 0.92 | 1049.7586 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 120 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 3 | YES | 9.8832 | 0.089847 | YES | NA | NA | NA | 3R X 11kV X 1C X 400 Sqmm | 1080 |  | 6
13015
| 11 KV STATION SWGR-3SA | [37 empty] | 0
1 | CW Pump Motor | M |  | 4325 | 11 | 0.77 | 0.945 | 311.9773 | 2246.2366 | 0.2 | 50 | 0.16 | 212.766 | AIR | 1C | 300 | 387 | 0.162 | 0.088 | 750 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 2 | YES | 36.6542 | 0.33322 | YES | 173.0664 | 1.5733 | YES | 2R X 11kV X 1C X 300 Sqmm | 4500 |  | 4
2 | Lighting Service Transformer | F | 630 |  | 11 | 0.77 | 0.945 | 33.0674 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 150 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 1.554 | 0.014128 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 150 |  | 2
3 | 11/0.433kV Raw Water Service Transformer feeder#1 | F | 630 |  | 11 | 0.77 | 0.945 | 33.0674 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 2000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.7205 | 0.18837 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 2000 |  | 2
4 | Station Service Transformer Feeder | F | 2500 |  | 11 | 0.77 | 0.945 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 150 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 6.1668 | 0.056062 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 150 |  | 2
5 | Switchyard Service Transformer Feeder | F | 750 |  | 11 | 0.88 | 0.95 | 39.3659 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 400 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 5.0281 | 0.04571 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 400 |  | 2
6 | 11/0.433kV AWRS Service Transformer feeder#1 | F | 630 |  | 11 | 0.88 | 0.95 | 33.0674 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 200 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 2.1118 | 0.019198 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 200 |  | 2
7 | 11/0.433kV Fuel Oil Service Transformer feeder#1 | F | 750 |  | 11 | 0.83 | 0.93 | 39.3659 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 250 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 3.1287 | 0.028442 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 250 |  | 2
8 | 11/0.433kV WTP Service Transformer feeder#1 | F | 2000 |  | 11 | 0.75 | 0.97 | 104.9759 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 535 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 17.4811 | 0.15892 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 535 |  | 2
9 | 11/0.433kV CHP Service Transformer feeder#1 (Bunker Bay) | F | 2000 |  | 11 | 0.85 | 0.92 | 104.9759 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 1000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 33.4659 | 0.30424 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 1000 |  | 2
10 | 11/0.433kV Misc Service Transformer feeder#1 | F | 1000 |  | 11 | 0.88 | 0.95 | 52.4879 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 575 | 0.1018 | 0.0937 | 650 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 1 | YES | 7.9237 | 0.072033 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 650 |  | 2
11 | 11/6.9kV AHP Auxiliary Transformer Feeder#1 | F | 14000 |  | 11 | 0.75 | 0.97 | 734.831 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 600 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 52.8172 | 0.48016 | YES | NA | NA | NA | 2R X 11kV X 1C X 400 Sqmm | 3600 |  | 4
12 | 11/6.9kV CHP Auxiliary Transformer Feeder#1 | F | 14000 |  | 11 | 0.83 | 0.93 | 734.831 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 450 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 39.1632 | 0.35603 | YES | NA | NA | NA | 2R X 11kV X 1C X 400 Sqmm | 2700 |  | 4
13 | 11/6.9kV FGD Auxiliary Transformer Feeder#1 | F | 20000 |  | 11 | 0.83 | 0.93 | 1049.7586 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 387 | 0.162 | 0.088 | 490 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 5 | YES | 32.705 | 0.29732 | YES | NA | NA | NA | 5R X 11kV X 1C X 400 Sqmm | 7350 |  | 10
14 | Colony Area Switchgear | F | 2500 |  | 11 | 0.83 | 0.93 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 2000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 83.4312 | 0.75847 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 2000
15 | River Water Intake Pump House Feeder -1 | F | 6500 |  | 11 | 0.83 | 0.93 | 341.1715 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 387 | 0.162 | 0.088 | 2000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 2 | YES | 108.4605 | 0.986 | YES | NA | NA | NA | 2R X 11kV X 1C X 400 Sqmm | 12000
| 11 KV STATION SWGR-4SA | [37 empty] | 0
1 | Lighting Service Transformer | F | 630 |  | 11 | 0.77 | 0.945 | 33.0674 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 150 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 1.554 | 0.014128 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 150 |  | 2
2 | 11/0.433kV Raw Water Service Transformer feeder#1 | F | 630 |  | 11 | 0.77 | 0.945 | 33.0674 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 2000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 20.7205 | 0.18837 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 2000
3 | Switchyard Service Transformer Feeder | F | 750 |  | 11 | 0.88 | 0.95 | 39.3659 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 400 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 5.0281 | 0.04571 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 400 |  | 2
4 | 11/0.433kV AWRS Service Transformer feeder#1 | F | 630 |  | 11 | 0.83 | 0.93 | 33.0674 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 200 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 2.1025 | 0.019113 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 200 |  | 2
5 | 11/0.433kV Fuel Oil Service Transformer feeder#1 | F | 750 |  | 11 | 0.77 | 0.945 | 39.3659 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 250 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 3.0834 | 0.028031 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 250 |  | 2
6 | WTP Service Transformer Feeder | F | 2000 |  | 11 | 0.85 | 0.92 | 104.9759 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 535 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 17.9042 | 0.16277 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 535 |  | 2
7 | CHP Service Transformer Feeder | F | 2000 |  | 11 | 0.75 | 0.97 | 104.9759 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 1000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 32.6749 | 0.29704 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 1000 |  | 2
8 | 11/0.433kV Misc Service Transformer feeder#1 | F | 1000 |  | 11 | 0.77 | 0.945 | 52.4879 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 650 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 10.6891 | 0.097174 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 650 |  | 2
9 | Station Service Transformer Feeder | F | 2500 |  | 11 | 0.77 | 0.945 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 150 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 6.1668 | 0.056062 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 150 |  | 2
10 | AHP Auxiliary Transformer Feeder | F | 14000 |  | 11 | 0.88 | 0.95 | 734.831 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 600 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 51.1991 | 0.46545 | YES | NA | NA | NA | 2R X 11kV X 1C X 400 Sqmm | 3600 |  | 4
11 | CHP Auxiliary Transformer Feeder | F | 14000 |  | 11 | 0.75 | 0.97 | 734.831 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 450 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 2 | YES | 39.6129 | 0.36012 | YES | NA | NA | NA | 2R X 11kV X 1C X 400 Sqmm | 2700 |  | 4
12 | FGD Auxiliary Transformer Feeder | F | 20000 |  | 11 | 0.83 | 0.93 | 1049.7586 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 575 | 0.1018 | 0.0937 | 490 | 0.89 | 0.78 | NA | 0 | 0 | 0.6942 | 399.165 | 3 | YES | 40.6137 | 0.36922 | YES | NA | NA | NA | 3R X 11kV X 1C X 400 Sqmm | 4410 |  | 6
13 | Colony Area Switchgear Feeder | F | 2500 |  | 11 | 0.83 | 0.93 | 131.2198 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 3C | 240 | 387 | 0.162 | 0.088 | 2000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 1 | YES | 83.4312 | 0.75847 | YES | NA | NA | NA | 1R X 11kV X 3C X 240 Sqmm | 2000 |  | 2
14 | River Water Intake Pump House Feeder -1 | F | 6500 |  | 11 | 0.83 | 0.93 | 341.1715 | 0 | 0 | 50 | 0.16 | 212.766 | AIR | 1C | 400 | 387 | 0.162 | 0.088 | 2000 | 0.89 | 0.73 | NA | 0 | 0 | 0.6497 | 251.4339 | 2 | YES | 108.4605 | 0.986 | YES | NA | NA | NA | 2R X 11kV X 1C X 400 Sqmm | 12000
[42 empty] | Row Labels | Sum of Total Length in meters
[42 empty] | 2R X 11kV X 1C X 400 Sqmm | 26400
[42 empty] | 3R X 11kV X 1C X 400 Sqmm | 17100
[42 empty] | Grand Total | 43500

## BOQ
BOQ
Sl.No | Type of Cable | Length As per Calculation | Margin (10%) | Total Length | Rounded Up (length in M) | 3C X 240 | 475
1 | 3C X 240 | 27560 | 2756 | 30316 | 40000 | 3C X 300 | 500
2 | 3C x 300 | 2000 | 200 | 2200 | 2500 | 1C X 300 | 4500
3 | 1C x 400 | 49590 | 4959 | 54549 | 70000 | 1C X 300 | 2460
[6 empty] | 1C X 400 | 765
[6 empty] | 3C X 240 | 460
[6 empty] | 3C X 240 | 470
[6 empty] | 3C X 240 | 460
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 1100
[6 empty] | 1C X 400 | 1080
[6 empty] | X | 0
[6 empty] | X | 0
[6 empty] | 3C X 240 | 475
[6 empty] | 3C X 300 | 500
[6 empty] | 1C X 300 | 4500
[6 empty] | 1C X 400 | 2460
[6 empty] | 1C X 400 | 1080
[6 empty] | 3C X 240 | 470
[6 empty] | 3C X 240 | 460
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 1100
[6 empty] | X | 0
[6 empty] | X | 0
[6 empty] | 3C X 240 | 475
[6 empty] | 3C X 300 | 500
[6 empty] | 1C X 300 | 4500
[6 empty] | 1C X 400 | 2460
[6 empty] | 1C X 400 | 765
[6 empty] | 3C X 240 | 470
[6 empty] | 3C X 240 | 470
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 1100
[6 empty] | 1C X 400 | 1080
[6 empty] | X | 0
[6 empty] | X | 0
[6 empty] | 3C X 240 | 475
[6 empty] | 3C X 300 | 500
[6 empty] | 1C X 300 | 4500
[6 empty] | 1C X 400 | 2460
[6 empty] | 3C X 240 | 470
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 490
[6 empty] | 3C X 240 | 1100
[6 empty] | 1C X 400 | 1080
[6 empty] | X | 13015
[6 empty] | X | 0
[6 empty] | 1C X 300 | 4500
[6 empty] | 3C X 240 | 150
[6 empty] | 3C X 240 | 2000
[6 empty] | 3C X 240 | 150
[6 empty] | 3C X 240 | 400
[6 empty] | 3C X 240 | 200
[6 empty] | 3C X 240 | 250
[6 empty] | 3C X 240 | 535
[6 empty] | 3C X 240 | 1000
[6 empty] | 3C X 240 | 650
[6 empty] | 1C X 400 | 3600
[6 empty] | 1C X 400 | 2700
[6 empty] | 1C X 400 | 7350
[6 empty] | X | 0
[6 empty] | X | 0
[6 empty] | 3C X 240 | 150
[6 empty] | 3C X 240 | 400
[6 empty] | 3C X 240 | 200
[6 empty] | 3C X 240 | 250
[6 empty] | 3C X 240 | 535
[6 empty] | 3C X 240 | 1000
[6 empty] | 3C X 240 | 650
[6 empty] | 3C X 240 | 150
[6 empty] | 1C X 400 | 3600
[6 empty] | 1C X 400 | 2700
[6 empty] | 1C X 400 | 4410
[6 empty] | 3C X 240 | 2000
[6 empty] | 1C X 400 | 12000
[6 empty] | X | 0
[6 empty] | X | 0

## Catalogue
KEC Cable Catalogue
Multi core cable |  |  |  | 11/11kV |  |  | Single core cable |  |  |  | 11/11kV
Size in mm2 | Current carrying capacity |  |  | Resistance Ohm/km | Reactance Ohm/km | Cable Dia | Size in mm2 | Current carrying capacity |  |  | Resistance Ohm/km | Reactance Ohm/km | Cable Dia | XLPE | Ambient temperature (K1) 50°C | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temprature (K3) 30°C | Depth of laying (K4) (1500 mm) |  | Thermal resistivity of ground (1.5 °C.m/W) (K5)
| Air | Ground | Duct |  |  |  |  | Air | Ground | Duct | [5 empty] | Single core | Multi core |  | Single core | Multi core | Single core | Multi core
3C X 120 | 256 | 216 | 188 | 0.325 | 0.097 | 55 | 1C X 150 | 335 | 255 | 215 | 0.2648 | 0.1058 | 30 | AIR | 0.89 | 0.78 | 0.73
3C X 150 | 288 | 242 | 209 | 0.265 | 0.094 | 58 | 1C X 185 | 384 | 284 | 238 | 0.2112 | 0.1 | 33 | Duct |  | 0.75 | 0.8 | 1 | 0.94 | 0.96 | 1 | 1
3C X 185 | 330 | 273 | 240 | 0.211 | 0.091 | 61 | 1C X 240 | 446 | 323 | 270 | 0.1615 | 0.098 | 35 | Ground |  | 0.73 | 0.77 | 1 | 0.94 | 0.95 | 1 | 1
3C X 240 | 387 | 315 | 278 | 0.162 | 0.088 | 67 | 1C X 300 | 503 | 357 | 297 | 0.1297 | 0.0974 | 37
3C X 300 | 441 | 354 | 312 | 0.13 | 0.086 | 71 | 1C X 400 | 575 | 397 | 329 | 0.1018 | 0.0937 | 40
3C X 400 | 512 | 404 | 356 | 0.102 | 0.082 | 76 | 1C X 500 | 647 | 436 | 360 | 0.0802 | 0.0918 | 43
[7 empty] | 1C X 630 | 725 | 476 | 390 | 0.0636 | 0.0901 | 47