## Basis & Assumptions (2) (hidden)
Assumptions and Inputs considered for MV & LV cable sizing
1) | All MV & LV cables are considered to be laid in Air / Trench with cover Cable Tray and de-rated accordingly.
2) | All MV & LV multi-core cables are considered to be laid on touching formation and de-rated accordingly.
3) | All MV single core cables are considered to be laid in Trefoil Formation with 150mm spacing and de-rated accordingly.
4) | All LV single core cables are considered to be laid in Trefoil Formation and de-rated accordingly.
5) | Over all de-rating factor considered as mentioned below based on laying condition & method of installation: LV Multi core cable - 0.66 LV Single core cable - 0.9 MV Multi core cable - 0.664 MV Single core cable - 0.819
6) | The % voltage drop is limited to 3% for outgoing motor feeders , 2.5% for outgoing Power feeders and 2% to incoming feeders.
7) | The % voltage drop is limited to 15% for motor feeders during starting.
8) | For both MV & LV Cable sizing all required datas are taken from reference Catalogue (KEC/RPG Make Catalogue). Further final Cable sizing/BOQ shall be updated based on final vendor data during Detail Engg. Stage.
9) | Desalination package both MV & LV power cable has kept under hold & same shall be revised after the finaliziation of scope.
10) | Wherever the location of load is unknown, an approximate location is assumed and % voltage drop is calculated.
11) | This cable sizing is done based on the "Electrical Load List, Rev-1". And same will be revised after finalization of final Loas list.
12) | The below mentioned pachages are part of Vendor scope, henece respective package Cable sizing / cable boq has not included. 1. Ammonia Storage area, 2. ASU Package, 3. Nitrogen Package, 4. Flare area Package, 5. Cooling tower Package. 6. ETP Package. 7. Desalination Sea Water Treatment Package. 8. Sea Water Intake system. 9. Electrolyzer Area Package.
from ups sub db to I&C instrument cable lnot considered

## Basis & Assumptions
Basis & Assumptions considered for MV & LV cable sizing
1) | All MV & LV cables are considered to be laid in Air / Trench with cover Cable Tray and de-rated accordingly.
2) | All MV & LV multi-core cables are considered to be laid on touching formation and de-rated accordingly.
3) | All MV single core cables are considered to be laid in Trefoil Formation with 150mm spacing and de-rated accordingly.
4) | All LV single core cables are considered to be laid in Trefoil Formation and de-rated accordingly.
5) | Over all de-rating factor considered as mentioned below based on laying condition & method of installation: LV Multi core cable - 0.587 LV Single core cable - 0.721 MV Multi core cable - 0.599 MV Single core cable - 0.738
6) | The % voltage drop is limited to 3% for outgoing motor feeders , 2.5% for outgoing Power feeders and 2% to incoming feeders.
7) | The % voltage drop is limited to 15% for motor feeders during starting.
8) | For both MV & LV Cable sizing all required datas are taken from reference Catalogue (KEC/RPG Make Catalogue). Further final Cable sizing/BOQ shall be updated based on final vendor data during Detail Engg. Stage.
9) | 1). All incoming cable from solar, Grid, BESS to 33kV Switchgear (MSB) cable is part of Vendor/ACME scope henace same sizing/BOQ not considered. 2). In Desalination package: a) Incoming Cable from LV VFD to PMCC-4, 11kV Switchgaer to MV VFD's, both MV & LV power cables are inculded in the sizing/BOQ. b) Further from PMCC to Motor/LCS, from LV VFD to motor/LCS, from MV VFD to motor/LCS both MV & LV power cable BOQ is part of Vendor/ACME scope hence same has not included in the sizing/BOQ.
10) | Wherever the location of load is unknown, an approximate location is assumed and % voltage drop is calculated.
11) | This cable sizing is done based on the "Electrical Load List, Rev-1". And same will be revised after finalization of final Loas list.
12) | Cable from UPS DB/ Sub UPS DB to Instrument is not included in this sizing & same shall be considered in Instrument cable schedule/BOQ.
13) | The below mentioned packages are part of Vendor scope, henece respective package Cable sizing / cable boq has not included. 1. Ammonia Storage area, 2. ASU Package, 3. Nitrogen Package, 4. Flare area Package, 5. Cooling tower Package. 6. ETP Package. 7. Desalination Sea Water Treatment Package. 8. Sea Water Intake system. 9. Electrolyzer Area Package.

## Tray Sizing (hidden)
Cable Tray Sections |  | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | G1 | G2 | G3 | G4 | H | I | J | J1 | J2 | J3 | K | L | L1 | L2 | L3 | L4 | M | N | O | O1 | P | Q | Q1 | Q2 | Q3 | R | R1 | R2 | S | T
33kV MV Power Cable Trays
MV Cable sizing-33kV | Total Cable Dia | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Cable Tray Dia required with 20% Margin | with 20% marging | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
33kV MV Power Cable Trays |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11kV MV Power Cable Trays
MV Cable sizing-11kV |  | 0 | 1979 | 0 | 0 | 1550 | 1336 | 0 | 0 | 0 | 1336 | 0 | 772 | 618 | 464 | 263 | 139 | 0 | 564 | 564 | 0 | 0 | 0 | 0 | 132 | 666 | 308 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 0 | 429 | 0 | 305 | 305 | 0 | 0 | 0
Total Cable Tray Dia required with 20% Margin |  | 0 | 2374.8 | 0 | 0 | 1860 | 1603.2 | 0 | 0 | 0 | 1603.2 | 0 | 926.4 | 741.6 | 556.8 | 315.6 | 166.8 | 0 | 676.8 | 676.8 | 0 | 0 | 0 | 0 | 158.4 | 799.2 | 369.6 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514.8 | 0 | 514.8 | 0 | 366 | 366 | 0 | 0 | 0
11kV Power Cables - Ladder Type Tray | 600 | 0 | 3.958 | 0 | 0 | 3.1 | 2.672 | 0 | 0 | 0 | 2.672 | 0 | 1.544 | 1.236 | 0.928 | 0.526 | 0.278 | 0 | 1.128 | 1.128 | 0 | 0 | 0 | 0 | 0.264 | 1.332 | 0.616 | 0 | 0 | 0 | 0.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.858 | 0 | 0.858 | 0 | 0.61 | 0.61 | 0 | 0 | 0
|  | 0 | 4 | 0 | 0 | 4 | 2 | 0 | 0 | 0 | 2 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 450 | [13 empty] | 1 | [9 empty] | 1 |  | 1 | [14 empty] | 1
| 300 | [5 empty] | 1 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | 1 | 1 | 0 | [10 empty] | 0 | 0 | 1 | [12 empty] | 1 |  | 1 | 1 | 0
LV Power Cable Trays
LV Cable sizing_SS-1_Power Cables |  | 719 | #N/A | #N/A | 697 | 3779 | 3584 | 95 | 21 | 515 | 3489 | 0 | 3196 | 3066 | 2037 | 991 | 763 | 0 | 293 | 293 | 0 | 0 | 0 | 0 | 194 | 179 | 179 | 0 | 0 | 0 | 0 | 857 | 86 | 86 | 36 | 0 | 744 | 229 | 229 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Cable sizing_SS-2_Power Cables |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 2270 | 2270 | 2249 | 0 | 0 | 0
LV Cable sizing_SS-3_Power Cables |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Cable sizing_SS-4_Power Cables |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
LV Cable sizing_SS-5_Power Cables
LV Cable sizing_SS-6_Power Cables
Total Cable Tray Dia required for LV power Cable |  | #REF! | #N/A | #N/A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Cable Tray Dia required with 20% Margin |  | #REF! | #N/A | #N/A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
LV Power Cables - Ladder Type Tray | 600 | #REF! | #N/A | #N/A | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | #REF! | 10 | #N/A | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | 7 | 4 | 3 | 2 | 1 | 0 | #REF! | #REF! | 1 | 0 | 1 | 0 | 1 | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | 5 | 5 | 4 | #REF! | 2 | #REF!
| 450 | [12 empty] | 1 |  |  |  | #REF! | [23 empty] | #REF!
| 300 | [7 empty] | #REF! | [5 empty] | 1 | 1 | 1 |  |  |  | 1 | #REF! | 1 | #REF! | 1 |  |  |  |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  |  | #REF! | 1 |  |  | 1 |  | 1
LV Control Cables - Ladder Type Tray | 600 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0
| 450 | [16 empty] | 1
| 300 | [17 empty] | #REF! |  |  | #REF! |  | #REF! |  | 0 | 0 |  |  | #REF! | [7 empty] | 0 | #REF! | #REF! |  | 1 | #REF! | 1 | 1 | 1 | 1 | 0 | 1 | 1
Instrumentation Cable Trays |  | 1 | 3 | 3 | 14 | 8 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [19 empty] | 2 | 2 |  | 2 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1
|  | 1 | 2 | 12 | 2 | 8 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [19 empty] | 2 | 2 |  | 2
Instrumentation Cable Trays
IS Cable Tray | Total Cable Dia
600
450
300
Non IS Cable Tray | Total Cable Dia
600
450
300
F&G Cable Tray | Total Cable Dia
600
450
300
FOC & Telecom Cable Tray | Total Cable Dia
600
450
300
133.5
136.5
172.5
189.5
214.5
204.5
SS-2 to Admin
SS-2 to Canteen
SS-2 to Fire room
SS-2 to Store
SS-2 to OHC
SS-2 to Whorehouse

## Catalogue Aluminium
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (50°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 370 | 290 | 224 | 0.21 | 0.0875 | 26 | 690/400V | AIR | 0.89 | 0.81 | 0.66 | NA | NA | NA
1C X 240 | 445 | 340 | 283 | 0.16 | 0.0866 | 28 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 514 | 382 | 317 | 0.128 | 0.0857 | 31 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 605 | 437 | 370 | 0.1 | 0.0855 | 34 |  | Trench with cover | 0.89 | 0.81 | 0.66 | NA | NA | NA | 4 | 1.09 | 1.05 |  |  |  |  | 0.76
1C X 500 | 704 | 500 | 428 | 0.0774 | 0.0851 | 38 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 822 | 565 | 464 | 0.06 | 0.0843 | 42 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 62 | 70 | 57 | 3.94 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 79 | 90 | 75 | 2.44 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 108 | 117 | 99 | 1.54 | 0.0816 | 20 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 143 | 140 | 117 | 1.11 | 0.0794 | 21 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 173 | 168 | 143 | 0.82 | 0.0792 | 24 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 212 | 202 | 177 | 0.567 | 0.0752 | 27 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 257 | 243 | 217 | 0.41 | 0.0734 | 30
2C X 120 | 295 | 273 | 247 | 0.324 | 0.0726 | 32
2C X 150 | 342 | 310 | 305 | 0.264 | 0.0732 | 35
2C X 185 | 395 | 350 | 345 | 0.21 | 0.0727 | 39
2C X 240 | 465 | 401 | 393 | 0.16 | 0.0719 | 44
2C X 300 | 532 | 458 | 453 | 0.128 | 0.0711 | 48
2C X 400 | 622 | 505 | 553 | 0.1 | 0.0705 | 54
3-core cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13 | [15 empty] | 13.2
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14 | [15 empty] | 16.8
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15 | [15 empty] | 22.8
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16 | [15 empty] | 30.6
3C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 19 | [15 empty] | 36
3C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 19 | [15 empty] | 42
3C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 21 | [15 empty] | 57
3C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 23 | [15 empty] | 70.2
3C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 26 | [15 empty] | 84.6
3C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 30 | [15 empty] | 106.2
3C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 33 | [15 empty] | 132.6
3C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 35 | [15 empty] | 154.2
3C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 39 | [15 empty] | 175.8
3C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 43 | [15 empty] | 202.8
3C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 48 | [15 empty] | 240.6
3C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 53 | [15 empty] | 275.4
3C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 59 | [15 empty] | 321.6
4-core cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
4C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 21
3.5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 25
3.5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 27
3.5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 30
3.5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 36
3.5C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 39
3.5C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 43
3.5C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 48
3.5C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 53
3.5C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 58
3.5C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 64
3.5C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
5C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
5C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 20
5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 24
5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 26
5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 29
5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 33
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (50°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.125 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.73 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.12 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 324 | 252 | 240 | 0.325 | 0.115 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 368 | 281 | 267 | 0.265 | 0.114 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.73 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 424 | 317 | 303 | 0.211 | 0.109 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 502 | 367 | 350 | 0.161 | 0.105 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 577 | 414 | 397 | 0.13 | 0.102 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 673 | 470 | 451 | 0.102 | 0.098 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 757 | 519 | 493 | 0.08 | 0.096 | 46 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 876 | 586 | 557 | 0.063 | 0.094 | 50
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.09 | 54
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.088 | 58
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.097 | 49
3C X 95 | 238 | 24 | 180 | 0.411 | 0.093 | 52
3C X 120 | 274 | 232 | 206 | 0.325 | 0.09 | 56
3C X 150 | 309 | 259 | 231 | 0.265 | 0.088 | 58
3C X 185 | 354 | 293 | 262 | 0.211 | 0.085 | 63
3C X 240 | 415 | 338 | 304 | 0.162 | 0.083 | 69
3C X 300 | 472 | 380 | 343 | 0.13 | 0.082 | 75
3C X 400 | 545 | 432 | 393 | 0.102 | 0.08 | 84
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 6/10 (12)kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (50°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.125 | 27 | 6600V | AIR | 0.82 | 0.9 | 0.73 | NA | NA | NA | [7 empty] | AIR | 0.89 | 0.81 | 0.66 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.12 | 29 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05 |  |  |  |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98
1C X 120 | 324 | 252 | 240 | 0.325 | 0.115 | 30 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05 |  |  |  |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98
1C X 150 | 368 | 281 | 267 | 0.265 | 0.114 | 33 |  | Trench with cover | 0.82 | 0.9 | 0.73 | NA | NA | NA | 185 | 1.09 | 1.05 |  |  |  |  | Trench with cover | 0.89 | 0.81 | 0.66 | NA | NA | NA
1C X 185 | 424 | 317 | 303 | 0.211 | 0.109 | 34 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 502 | 367 | 350 | 0.161 | 0.105 | 36 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 577 | 414 | 397 | 0.13 | 0.102 | 39 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 673 | 470 | 451 | 0.102 | 0.098 | 42 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 757 | 519 | 493 | 0.08 | 0.096 | 46 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 876 | 586 | 557 | 0.063 | 0.094 | 50
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.09 | 54
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.088 | 59
Three core cable |  |  |  | 6/10 (12)kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14 | (LV Cable)
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15 | (LV Cable)
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16 | (LV Cable)
3C X 70 | 196 | 171 | 150 | 0.568 | 0.103 | 52
3C X 95 | 238 | 204 | 180 | 0.411 | 0.099 | 55
3C X 120 | 274 | 232 | 206 | 0.325 | 0.095 | 59
3C X 150 | 309 | 259 | 231 | 0.265 | 0.093 | 62
3C X 185 | 354 | 293 | 262 | 0.211 | 0.089 | 66
3C X 240 | 415 | 338 | 304 | 0.162 | 0.087 | 72
3C X 300 | 472 | 380 | 343 | 0.13 | 0.084 | 78
3C X 400 | 545 | 432 | 393 | 0.102 | 0.081 | 84
HV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (50°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 150mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1500 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.5 K.m/W) (K5) |  |  | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core | Single core | Single core | Multi core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.146 | 38 | 33000V | AIR | 0.82 | 0.9 | 0.73 | NA | NA | NA | [7 empty] | AIR | 0.89 | 0.81 | 0.66 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.14 | 39 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.95 | 120 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93 | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98
1C X 120 | 324 | 252 | 240 | 0.325 | 0.134 | 41 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.96 | 150 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93 | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98
1C X 150 | 368 | 281 | 267 | 0.265 | 0.132 | 43 |  | Trench with cover | 0.82 | 0.9 | 0.73 | NA | NA | NA | 185 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93 | Trench with cover | 0.89 | 0.81 | 0.66 | NA | NA | NA
1C X 185 | 424 | 317 | 303 | 0.211 | 0.126 | 45 | [8 empty] | 240 | 1.09 | 1.05 | 1.14 | 0.91 | 1.1 | 0.93
1C X 240 | 502 | 367 | 350 | 0.161 | 0.122 | 47 | [8 empty] | 300 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 300 | 577 | 414 | 397 | 0.13 | 0.118 | 50 | [8 empty] | 400 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 400 | 673 | 470 | 451 | 0.102 | 0.113 | 53 | [8 empty] | 500 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 500 | 757 | 519 | 493 | 0.08 | 0.109 | 56 | [8 empty] | 630 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 630 | 876 | 586 | 557 | 0.063 | 0.105 | 60
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.101 | 65
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.099 | 69
Three core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.129 | 76
3C X 95 | 238 | 204 | 180 | 0.411 | 0.124 | 79
3C X 120 | 274 | 232 | 206 | 0.325 | 0.119 | 83
3C X 150 | 309 | 259 | 231 | 0.265 | 0.115 | 86
3C X 185 | 354 | 293 | 262 | 0.211 | 0.11 | 90
3C X 240 | 415 | 338 | 304 | 0.162 | 0.106 | 88
3C X 300 | 472 | 380 | 343 | 0.13 | 0.103 | 93
3C X 400 | 545 | 432 | 393 | 0.102 | 0.098 | 100

## MV Cable sizing-11kV
MV (11kV) POWER CABLE SIZING
Sl. No |  |  | LOAD | [12 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  | CABLE DATA | [14 empty] | DERATING FACTOR | [5 empty] | CURRENT CARRYING CAPACITY |  |  | RUNNING CONDITION VOLTAGE DROP |  | MOTOR STARTING VOLTAGE DROP |  | Selected Cable Size
| Tag No. | From | Description | Equipment Location | BUS | Type of feeder | Rated power | UNIT (kW / kVA) | 3Phase / 1Phase | Rated Voltage (V) | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard (kA) | Short circuit current withstand duration (sec) | Minimum size required for Short circuit withstand capacity (Sq.mm) | Installation | No. of Cores | Size in (Sq.mm) | Cable size | Cable size With (PE) Core | Cable Voltage (kV) | Current Rating of the Cable (A) | Cable resistance at 90°C (Ohm / Ph / km) | Cable reactance at 50Hz (Ohm / Ph / km) | Cable Length with in Electrical Building (m) | Cable Length from Electrical Building to Equipment (m) | Cable length Riser & Dropper (m) | Cable length both side dropping & Termination (m) | Spare 10% | Cable length for each run (m) | Ambient temperature (K1) | Grouping factor (K2) | Ground temperature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | Derated current carrying capacity (A) | No. of Runs | Derated current > Rated current | % VOLTAGE DROP DURING RUNNING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT (YES/NO) | % VOLTAGE DROP DURING STARTING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT DURING STARTING CONDITION (YES/NO) | Selected cable size | Selected cable size | Total Cable Length in meters | Remarks | No. of End Termination | Cable Route(Sections) | Dia of the conductor (mm) | Total Dia of the conductor (mm) | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | IA | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | TA | T1.A | U |  | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | IA | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | TA | T1.A | U
|  |  | MAIN SUBSTATION |  |  | VFD | [33 empty] | A
|  |  | 11kV MV Switchgear-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1401-B102 | 11kV MV Switchgear-1 | START-UP HEATER | AMMONIA PLANT | B | POWER | 3200 | kW | 3Ph | 11000 | 0.85 | 0.95 | 208.0017 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 299 | 38 | 10 | 42 | 460 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 2 | YES | 0.20658 | YES | NA | NA | 2R x 6/10 (12)kV x 3C x 150 Sqmm | 2R x 6/10 (12)kV x 3C x 150 Sqmm | 920 |  | 4 | ACDEE1E2E3 | 62 | 124 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 124 | 0 | 0 | 124 | 124 | 0 | 0 | 0 | 124 | 0 | 124 | 124 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1418-P003A | 11kV MV Switchgear-1 | MAIN FIRE PUMP-1 | FIRE WATER PUMP HOUSE | A | MOTOR | 500 | kW | 3Ph | 11000 | 0.87 | 0.955 | 31.5869 | 189.5213 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 48 | 214 | 20 | 6 | 29 | 320 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.043991 | YES | 0.13763 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1418-P003B | 11kV MV Switchgear-1 | MAIN FIRE PUMP-2 | FIRE WATER PUMP HOUSE | B | MOTOR | 500 | kW | 3Ph | 11000 | 0.87 | 0.955 | 31.5869 | 189.5213 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 49 | 214 | 20 | 6 | 29 | 320 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.043991 | YES | 0.13763 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1402-P002A | 11kV MV Switchgear-1 | AMMONIA TRANSFER PUMP | AMMONIA STORAGE AREA | A | MOTOR | 355 | kW | 3Ph | 11000 | 0.86 | 0.964 | 22.4757 | 134.8539 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 394 | 42 | 10 | 52 | 570 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.055546 | YES | 0.17444 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 570 |  | 2 | ACDEFGIJ | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1402-P002A | 11kV MV Switchgear-1 | AMMONIA TRANSFER PUMP-SPACE HEATER | AMMONIA STORAGE AREA | A | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 67 | 394 | 42 | 10 | 52 | 570 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.7559 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 570 |  | 2 | ACDEFGIJ | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1402-P002B | 11kV MV Switchgear-1 | AMMONIA TRANSFER PUMP | AMMONIA STORAGE AREA | B | MOTOR | 355 | kW | 3Ph | 11000 | 0.86 | 0.964 | 22.4757 | 134.8539 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 392 | 42 | 10 | 50 | 550 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.053597 | YES | 0.16831 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 550 |  | 2 | ACDEFGIJ | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1402-P002B | 11kV MV Switchgear-1 | AMMONIA TRANSFER PUMP-SPACE HEATER | AMMONIA STORAGE AREA | B | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 53 | 392 | 42 | 10 | 50 | 550 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.6943 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 550 |  | 2 | ACDEFGIJ | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1402-PK003A | 11kV MV Switchgear-1 | AMMONIA HOLDING COMPRESSOR | AMMONIA STORAGE AREA | A | MOTOR | 620 | kW | 3Ph | 11000 | 0.84 | 0.95 | 40.7801 | 244.6806 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 395 | 42 | 10 | 52 | 570 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.099942 | YES | 0.3165 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 570 |  | 2 | ACDEFGIJ | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1402-PK003A | 11kV MV Switchgear-1 | AMMONIA HOLDING COMPRESSOR-SPACE HEATER | AMMONIA STORAGE AREA | A | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 67 | 395 | 42 | 10 | 52 | 570 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.7559 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 570 |  | 2 | ACDEFGIJ | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1402-PK003B | 11kV MV Switchgear-1 | AMMONIA HOLDING COMPRESSOR | AMMONIA STORAGE AREA | B | MOTOR | 620 | kW | 3Ph | 11000 | 0.84 | 0.95 | 40.7801 | 244.6806 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 398 | 42 | 10 | 51 | 560 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.098189 | YES | 0.31094 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 560 |  | 2 | ACDEFGIJ | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1402-PK003B | 11kV MV Switchgear-1 | AMMONIA HOLDING COMPRESSOR-SPACE HEATER | AMMONIA STORAGE AREA | B | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 53 | 398 | 42 | 10 | 51 | 560 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.7251 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 560 |  | 2 | ACDEFGIJ | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1401-JT301 | 11kV MV Switchgear-1 | STEAM TURBINE GENERATOR | AMMONIA PLANT | A | MOTOR | 2300 | kW | 3Ph | 11000 | 0.85 | 0.95 | 149.5012 | 897.0073 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 335 | 38 | 10 | 45 | 500 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.32279 | YES | 1.0178 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 500 |  | 2 | ACDEE1E2E3E4E5 | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 62 | 62 | 62 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1401-JT301 | 11kV MV Switchgear-1 | STEAM TURBINE GENERATOR-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 67 | 335 | 38 | 10 | 45 | 500 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.5403 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 500 |  | 2 | ACDEE1E2E3E4E5 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1401-CM103 | 11kV MV Switchgear-1 | MAIN MOTOR | AMMONIA PLANT | A | VFD | 5400 | kW | 3Ph | 11000 | 0.88 | 0.97 | 332.0464 | 332.0464 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 297 | 38 | 10 | 42 | 460 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 2 | YES | 0.33355 | FALSE | NA | NA | 2R x 6/10 (12)kV x 3C x 150 Sqmm | 2R x 6/10 (12)kV x 3C x 150 Sqmm | 920 |  | 4 | ACDEE1E2E3E4 | 62 | 124 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 124 | 0 | 0 | 124 | 124 | 0 | 0 | 0 | 124 | 0 | 124 | 124 | 124 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 1401-CM105 | 11kV MV Switchgear-1 | MAIN MOTOR | AMMONIA PLANT | B | VFD | 2000 | kW | 3Ph | 11000 | 0.88 | 0.97 | 122.9801 | 122.9801 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 314 | 38 | 10 | 42 | 460 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.24707 | FALSE | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 460 |  | 2 | ACDEE1E2E3E4E5 | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 62 | 62 | 62 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 1401-CM201 | 11kV MV Switchgear-1 | NITROGEN GAS COMPRESSOR MAIN MOTOR FOR 1401-J-201 | AMMONIA PLANT | B | MOTOR | 600 | kW | 3Ph | 11000 | 0.85 | 0.959 | 38.6343 | 231.8059 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 283 | 38 | 10 | 39 | 430 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.071737 | YES | 0.2262 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 430 |  | 2 | ACDEE1E2E3 | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 62 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 1401-CM201 | 11kV MV Switchgear-1 | NITROGEN GAS COMPRESSOR MAIN MOTOR FOR 1401-J-201-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 53 | 283 | 38 | 10 | 39 | 430 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.7662 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 430 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 1401-CM202A | 11kV MV Switchgear-1 | AUX. HYDROGEN COMPRESSOR MAIN MOTOR 1401-J-202B | AMMONIA PLANT | A | MOTOR | 2450 | kW | 3Ph | 11000 | 0.88 | 0.97 | 150.6507 | 903.9041 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 267 | 38 | 10 | 39 | 430 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.28292 | YES | 0.88204 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 430 |  | 2 | ACDEE1 | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 1401-CM202A | 11kV MV Switchgear-1 | AUX. HYDROGEN COMPRESSOR MAIN MOTOR 1401-J-202B-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 67 | 267 | 38 | 10 | 39 | 430 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.7662 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 430 |  | 2 | ACDEE1 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 1401-CM202B | 11kV MV Switchgear-1 | AUX. HYDROGEN COMPRESSOR MAIN MOTOR 1401-J-202B | AMMONIA PLANT | B | MOTOR | 2450 | kW | 3Ph | 11000 | 0.88 | 0.97 | 150.6507 | 903.9041 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 270 | 38 | 10 | 38 | 410 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.26977 | YES | 0.84101 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 410 |  | 2 | ACDEE1E2 | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 1401-CM202B | 11kV MV Switchgear-1 | AUX. HYDROGEN -SPACE HEATERCOMPRESSOR MAIN MOTOR 1401-J-202B | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 53 | 270 | 38 | 10 | 38 | 410 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.684 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 410 |  | 2 | ACDEE1E2 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 1401-CM203A | 11kV MV Switchgear-1 | AUX. HYDROGEN COMPRESSOR MAIN MOTOR 1401-J-203A | AMMONIA PLANT | A | MOTOR | 2450 | kW | 3Ph | 11000 | 0.88 | 0.97 | 150.6507 | 903.9041 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 256 | 38 | 10 | 38 | 410 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.26977 | YES | 0.84101 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 410 |  | 2 | ACDEE1 | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 1401-CM203A | 11kV MV Switchgear-1 | AUX. HYDROGEN COMPRESSOR MAIN MOTOR 1401-J-203A-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 67 | 256 | 38 | 10 | 38 | 410 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.684 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 410 |  | 2 | ACDEE1 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 1401-CM203B | 11kV MV Switchgear-1 | AUX. HYDROGEN COMPRESSOR MAIN MOTOR 1401-J-203B | AMMONIA PLANT | B | MOTOR | 2450 | kW | 3Ph | 11000 | 0.88 | 0.97 | 150.6507 | 903.9041 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 262 | 38 | 10 | 37 | 400 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.26319 | YES | 0.8205 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 400 |  | 2 | ACDEE1E2 | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 1401-CM203B | 11kV MV Switchgear-1 | AUX. HYDROGEN COMPRESSOR MAIN MOTOR 1401-J-203B-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 53 | 262 | 38 | 10 | 37 | 400 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.6429 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 400 |  | 2 | ACDEE1E2 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 1407-PM001A | 11kV MV Switchgear-1 | COOLING WATER PUMP - A | COOLING TOWER AREA | A | MOTOR | 1100 | kW | 3Ph | 11000 | 0.87 | 0.967 | 68.6288 | 411.7728 | 0.2 | 31.5 | 0.16 | 134.0426 | TRENCH | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 176 | 20 | 6 | 27 | 300 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.089607 | YES | 0.28033 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 300 |  | 2 | AQQ2RR1 | 62 | 62 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 1407-PM001A | 11kV MV Switchgear-1 | COOLING WATER PUMP - A-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 67 | 176 | 20 | 6 | 27 | 300 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 1.9733 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 300 |  | 2 | AQQ2RR1 | 14 | 14 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 1407-PM001B | 11kV MV Switchgear-1 | COOLING WATER PUMP - B | COOLING TOWER AREA | B | MOTOR | 1100 | kW | 3Ph | 11000 | 0.87 | 0.967 | 68.6288 | 411.7728 | 0.2 | 31.5 | 0.16 | 134.0426 | TRENCH | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 181 | 20 | 6 | 26 | 290 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.08662 | YES | 0.27099 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 290 |  | 2 | AQQ2RR1 | 62 | 62 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 1407-PM001B | 11kV MV Switchgear-1 | COOLING WATER PUMP - B-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 53 | 181 | 20 | 6 | 26 | 290 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 1.9075 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 290 |  | 2 | AQQ2RR1 | 14 | 14 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 1407-PM001C | 11kV MV Switchgear-1 | COOLING WATER PUMP - C | COOLING TOWER AREA | A | MOTOR | 1100 | kW | 3Ph | 11000 | 0.87 | 0.967 | 68.6288 | 411.7728 | 0.2 | 31.5 | 0.16 | 134.0426 | TRENCH | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 186 | 20 | 6 | 28 | 310 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.092593 | YES | 0.28968 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 310 |  | 2 | AQQ2RR1 | 62 | 62 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 1407-PM001C | 11kV MV Switchgear-1 | COOLING WATER PUMP - C-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 67 | 186 | 20 | 6 | 28 | 310 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 22.7468 | 1 | YES | 1.2733 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 1R x 6/10 (12)kV x 3C x 4 Sqmm | 310 |  | 2 | AQQ2RR1 | 15 | 15 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 1407-PM001D | 11kV MV Switchgear-1 | COOLING WATER PUMP - D | COOLING TOWER AREA | B | MOTOR | 1100 | kW | 3Ph | 11000 | 0.87 | 0.967 | 68.6288 | 411.7728 | 0.2 | 31.5 | 0.16 | 134.0426 | TRENCH | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 191 | 20 | 6 | 27 | 300 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.089607 | YES | 0.28033 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 300 |  | 2 | AQQ2RR1 | 62 | 62 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 1407-PM001D | 11kV MV Switchgear-1 | COOLING WATER PUMP - D-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 53 | 191 | 20 | 6 | 27 | 300 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 1.9733 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 300 |  | 2 | AQQ2RR1 | 14 | 14 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 | [14 empty] | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ASU PACKAGE (1404-PK001) | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 1404-J110A | 11kV MV Switchgear-1 | CENTRIFUGAL AIR COMPRESSOR-A | AIR SEPARATION UNIT | A | MOTOR | 1400 | kW | 3Ph | 11000 | 0.81 | 0.961 | 94.4015 | 566.4092 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 100 | 22 | 10 | 20 | 220 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.088029 | YES | 0.28278 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 220 |  | 2 | AC | 62 | 62 |  | 1 |  |  | 1 | [65 empty] | 0 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 1404-J110A | 11kV MV Switchgear-1 | CENTRIFUGAL AIR COMPRESSOR-A-SPACE HEATER | AIR SEPARATION UNIT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 67 | 100 | 22 | 10 | 20 | 220 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 1.4471 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 220 |  | 2 | AC | 14 | 14 |  | 1 |  |  | 1 | [65 empty] | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 1404-J110B | 11kV MV Switchgear-1 | CENTRIFUGAL AIR COMPRESSOR-B | AIR SEPARATION UNIT | A | MOTOR | 1400 | kW | 3Ph | 11000 | 0.81 | 0.961 | 94.4015 | 566.4092 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 100 | 22 | 10 | 20 | 220 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.088029 | YES | 0.28278 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 220 |  | 2 | AC | 62 | 62 |  | 1 |  |  | 1 | [65 empty] | 0 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 1404-J110B | 11kV MV Switchgear-1 | CENTRIFUGAL AIR COMPRESSOR-B-SPACE HEATER | AIR SEPARATION UNIT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 67 | 100 | 22 | 10 | 20 | 220 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 1.4471 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 220 |  | 2 | AC | 14 | 14 |  | 1 |  |  | 1 | [65 empty] | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | LATER | 11kV MV Switchgear-1 | PURIFICATION ELECTRIC HEATER | AIR SEPARATION UNIT | B | POWER | 240 | kW | 3Ph | 11000 | 0.85 | 0.95 | 15.6001 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 |  | 6/10(12) | 309 | 0.265 | 0.093 | 58 | 158 | 22 | 10 | 25 | 273 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.01839 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SEA WATER TREATMENT & SEA WATER INTAKE FACILITY. | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 1409-SWG-2-0003 | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11KV SWITCHGEAR-3 (SEA WATER TREATMENT) | SEA WATER TREATMENT ELECTRICAL BUILDING | A | POWER | 3036.3266 | kW | 3Ph | 11000 | 0.85573 | 0.94463 | 197.1561 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 185 | 3C X 185 | 3C X 185 | 6/10(12) | 354 | 0.211 | 0.089 | 67 | 322 | 20 | 8 | 42 | 460 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 211.9044 | 1 | YES | 0.3236 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 460 |  | 2 | ACDEFGHH1 | 66 | 66 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 | 1 | [49 empty] | 0 | 66 | 0 | 0 | 66 | 66 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 66 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 1409-SWG-2-0003 | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11KV SWITCHGEAR-3 (SEA WATER TREATMENT) | SEA WATER TREATMENT ELECTRICAL BUILDING | B | POWER | 3036.3266 | kW | 3Ph | 11000 | 0.85573 | 0.94463 | 197.1561 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 185 | 3C X 185 | 3C X 185 | 6/10(12) | 354 | 0.211 | 0.089 | 53 | 322 | 20 | 8 | 41 | 450 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 211.9044 | 1 | YES | 0.31657 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 450 |  | 2 | ACDEFGHH1 | 66 | 66 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 | 1 | [49 empty] | 0 | 66 | 0 | 0 | 66 | 66 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 66 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | DISTRIBTION TRANSFORMER LOADS | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 1421-TFD-2-0001 (1421-SWG-4-0001) | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 1 (LV SWITCHGEAR-1 FOR MAIN SUBSTATION) | MAIN SUBSTATION BUILDING | A | POWER | 3150 | kVA | 3Ph | 11000 | 0.85043 | 0.95 | 174.0389 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 51 | 20 | 8 | 15 | 170 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.12778 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 170 |  | 2 |  | 62 | 62 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 1421-TFD-2-0002 (1421-SWG-4-0001) | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 2 (LV SWITCHGEAR-1 FOR MAIN SUBSTATION) | MAIN SUBSTATION BUILDING | B | POWER | 3150 | kVA | 3Ph | 11000 | 0.85043 | 0.95 | 174.0389 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 57 | 20 | 8 | 14 | 160 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.12027 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 160 |  | 2 |  | 62 | 62 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 1420-TFD-2-0003 (1420-SWG-4-0002) | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 3 (LV SWITCHGEAR-2 FOR COOLING TOWER AREA) | COOLING TOWER SUBSTATION | A | POWER | 3150 | kVA | 3Ph | 11000 | 0.85544 | 0.95 | 174.0389 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 103 | 20 | 8 | 20 | 220 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.16571 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 220 |  | 2 | AQQ2 | 62 | 62 |  | 1 | [43 empty] | 1 |  | 1 | [22 empty] | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 1420-TFD-2-0004 (1420-SWG-4-0002) | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 4 (LV SWITCHGEAR-2 FOR COOLING TOWER AREA) | COOLING TOWER SUBSTATION | B | POWER | 3150 | kVA | 3Ph | 11000 | 0.85544 | 0.95 | 174.0389 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 108 | 20 | 8 | 19 | 210 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.15818 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 210 |  | 2 | AQQ2 | 62 | 62 |  | 1 | [43 empty] | 1 |  | 1 | [22 empty] | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 1402-TFD-2-0005 (1402-SWG-4-0003) | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 5 (LV SWITCHGEAR-3 FOR NH3 STORAGE) | NH3 STORAGE AREA ELECTRICAL BUILDING | A | POWER | 1600 | kVA | 3Ph | 11000 | 0.84921 | 0.95 | 88.4007 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 343 | 20 | 8 | 44 | 490 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.18699 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 490 |  | 2 | ACDEFGIIA | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  | 1 | [45 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 1402-TFD-2-0006 (1402-SWG-4-0003) | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 6 (LV SWITCHGEAR-3 FOR NH3 STORAGE) | NH3 STORAGE SUBSTATION | B | POWER | 1600 | kVA | 3Ph | 11000 | 0.84921 | 0.95 | 88.4007 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 53 | 346 | 20 | 8 | 43 | 470 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.17935 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 470 |  | 2 | ACDEFGIIA | 62 | 62 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  | 1 | [45 empty] | 0 | 62 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 1404-TFD-2-0009 (1404-SWG-4-0005) | 11kV MV Switchgear-1 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 9 (ASU MCC PANEL) | ASU Package Electrical Building | A | POWER | 1600 | kVA | 3Ph | 11000 | 0.84921 | 0.95 | 88.4007 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 67 | 100 | 22 | 10 | 20 | 220 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.083952 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 220 |  | 2 | AC | 62 | 62 |  | 1 |  |  | 1 | [65 empty] | 0 | 62 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 1421-SWG-2-0001 | #REF! | 11kV SWITCHGEAR INCOMER 1 | MAIN SUBSTATION BUILDING | A | INCOMER | 40000 | kVA | 3Ph | 11000 | 0.88004 | 0.95821 | 2191.0863 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | LATER | 11kV MV Switchgear-1 | Power Transformer (33/11.5kV) -1 NGR | MAIN SUBSTATION BUILDING | A | POWER |  | kW | 1Ph | 11000 | 0.85573 | 0.94463 | 400 | 0 | 0.00 | 31.5 | 1 | 335.1064 | AIR | 1C | 400 | 1C X 400 | 1C X 400 | 6/10(12) | 673 | 0.102 | 0.098 | 10 | 0 | 0 | 8 | 2 | 20 | 0.82 | 0.9 | NA | NA | NA | 0.738 | 496.674 | 1 | YES | 0.017382 | YES | NA | NA | 1R x 6/10(12)kV x 1C x 400 Sqmm/Phase | 1R x 6/10(12)kV x 1C x 400 Sqmm/Phase | 50 |  | 2 |  | 42 | 42 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 1421-SWG-2-0001 | #REF! | 11kV SWITCHGEAR INCOMER 2 | MAIN SUBSTATION BUILDING | B | INCOMER | 40000 | kW | 3Ph | 11000 | 0.88004 | 0.95821 | 2489.7465 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | LATER | 11kV MV Switchgear-1 | Power Transformer (33/11.5kV) -2 NGR | MAIN SUBSTATION BUILDING | B | POWER |  | kW | 1Ph | 11000 | 0.85573 | 0.94463 | 400 | 0 | 0.00 | 31.5 | 1 | 335.1064 | AIR | 1C | 400 | 1C X 400 | 1C X 400 | 6/10(12) | 673 | 0.102 | 0.098 | 10 | 0 | 0 | 8 | 2 | 20 | 0.82 | 0.9 | NA | NA | NA | 0.738 | 496.674 | 1 | YES | 0.017382 | YES | NA | NA | 1R x 6/10(12)kV x 1C x 400 Sqmm/Phase | 1R x 6/10(12)kV x 1C x 400 Sqmm/Phase | 50 |  | 2 |  | 42 | 42 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 1421-SWG-2-0002 | 11kV MV Switchgear-1 | 11kV SWITCHGEAR - APFC FEEDER | MAIN SUBSTATION BUILDING | A | POWER | 3550 | kVA | 3Ph | 11000 | 0.88004 | 0.95821 | 194.4589 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 185 | 3C X 185 | 3C X 185 | 6/10(12) | 354 | 0.211 | 0.089 | 10 | 0 | 0 | 8 | 2 | 20 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 211.9044 | 1 | YES | 0.01396 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 20 |  | 2 |  | 66 | 66 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 1421-SWG-2-0002 | 11kV MV Switchgear-1 | 11kV SWITCHGEAR - APFC FEEDER | MAIN SUBSTATION BUILDING | B | POWER | 3550 | kVA | 3Ph | 11000 | 0.88004 | 0.95821 | 194.4589 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 185 | 3C X 185 | 3C X 185 | 6/10(12) | 354 | 0.211 | 0.089 | 10 | 0 | 0 | 8 | 2 | 20 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 211.9044 | 1 | YES | 0.01396 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 1R x 6/10 (12)kV x 3C x 185 Sqmm | 20 |  | 2 |  | 66 | 66 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 11kV MV Switchgear-3 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SEA WATER TREATMENT FACILITY MV MOTORS LOADS | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | LATER | 11kV MV Switchgear-3 | SWRO HP PUMP - A (VFD) | SEA WATER TREATMENT PLANT (DESAL) | A | MOTOR | 425 | kW | 3Ph | 11000 | 0.87 | 0.955 | 26.8489 | 161.0931 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 15 | 0 | 0 | 8 | 3 | 30 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.0035056 | YES | 0.010967 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 30 |  | 2 |  | 62 | 62 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | LATER | 11kV MV Switchgear-3 | SWRO HP PUMP - A (VFD)-SPACE HEATER | SEA WATER TREATMENT PLANT (DESAL) | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 15 | 0 | 0 | 8 | 3 | 30 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 0.19733 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 30 |  | 2 |  | 14 | 14 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | LATER | 11kV MV Switchgear-3 | SWRO HP PUMP - B (VFD) | SEA WATER TREATMENT PLANT (DESAL) | B | MOTOR | 425 | kW | 3Ph | 11000 | 0.87 | 0.955 | 26.8489 | 161.0931 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 20 | 0 | 0 | 8 | 3 | 40 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.0046741 | YES | 0.014623 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 40 |  | 2 |  | 62 | 62 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | LATER | 11kV MV Switchgear-3 | SWRO HP PUMP - B (VFD)-SPACE HEATER | SEA WATER TREATMENT PLANT (DESAL) | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 20 | 0 | 0 | 8 | 3 | 40 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 0.26311 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 40 |  | 2 |  | 14 | 14 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | LATER | 11kV MV Switchgear-3 | SWRO HP PUMP - C (VFD) | SEA WATER TREATMENT PLANT (DESAL) | B | MOTOR | 425 | kW | 3Ph | 11000 | 0.87 | 0.955 | 26.8489 | 161.0931 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 25 | 0 | 0 | 8 | 4 | 40 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.0046741 | YES | 0.014623 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 40 |  | 2 |  | 62 | 62 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | LATER | 11kV MV Switchgear-3 | SWRO HP PUMP - C (VFD)-SPACE HEATER | SEA WATER TREATMENT PLANT (DESAL) | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 25 | 0 | 0 | 8 | 4 | 40 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 16.7608 | 1 | YES | 0.26311 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 1R x 6/10 (12)kV x 3C x 2.5 Sqmm | 40 |  | 2 |  | 14 | 14 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SEA WATER INTAKE AND OUT FALLMV MOTORS LOADS | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 1406-PM-001A | 11kV MV Switchgear-3 | SEA WATER LIFTING PUMP-A | SEA WATER INTAKE FACILITY | A | MOTOR | 250 | kW | 3Ph | 11000 | 0.86 | 0.964 | 15.8279 | 94.9675 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 20 | 920 | 20 | 8 | 97 | 1070 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.07343 | YES | 0.2306 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1070 |  | 2 | H1IK | 62 | 62 | [20 empty] | 1 | 1 |  |  |  |  | 1 | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 1406-PM-001A | 11kV MV Switchgear-3 | SEA WATER LIFTING PUMP-A-SPACE HEATER | SEA WATER INTAKE FACILITY | A | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 920 | 20 | 8 | 97 | 1070 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 30.5286 | 1 | YES | 2.2104 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 6 Sqmm | 1R x 6/10 (12)kV x 3C x 6 Sqmm | 1070 |  | 2 | H1IK | 16 | 16 | [20 empty] | 1 | 1 |  |  |  |  | 1 | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 1406-PM-001B | 11kV MV Switchgear-3 | SEA WATER LIFTING PUMP-B | SEA WATER INTAKE FACILITY | B | MOTOR | 250 | kW | 3Ph | 11000 | 0.86 | 0.964 | 15.8279 | 94.9675 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 20 | 920 | 20 | 8 | 97 | 1070 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.07343 | YES | 0.2306 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1070 |  | 2 | H1IK | 62 | 62 | [20 empty] | 1 | 1 |  |  |  |  | 1 | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 1406-PM-001B | 11kV MV Switchgear-3 | SEA WATER LIFTING PUMP-B-SPACE HEATER | SEA WATER INTAKE FACILITY | B | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 920 | 20 | 8 | 97 | 1070 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 30.5286 | 1 | YES | 2.2104 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 6 Sqmm | 1R x 6/10 (12)kV x 3C x 6 Sqmm | 1070 |  | 2 | H1IK | 16 | 16 | [20 empty] | 1 | 1 |  |  |  |  | 1 | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 1406-PM-001C | 11kV MV Switchgear-3 | SEA WATER LIFTING PUMP-C | SEA WATER INTAKE FACILITY | A | MOTOR | 250 | kW | 3Ph | 11000 | 0.86 | 0.964 | 15.8279 | 94.9675 | 0.2 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 6/10(12) | 309 | 0.265 | 0.093 | 20 | 920 | 20 | 8 | 97 | 1070 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.07343 | YES | 0.2306 | YES | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1070 |  | 2 | H1IK | 62 | 62 | [20 empty] | 1 | 1 |  |  |  |  | 1 | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 1406-PM-001C | 11kV MV Switchgear-3 | SEA WATER LIFTING PUMP-C-SPACE HEATER | SEA WATER INTAKE FACILITY | A | POWER | 0.15 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.80765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 920 | 20 | 8 | 97 | 1070 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 30.5286 | 1 | YES | 2.2104 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 6 Sqmm | 1R x 6/10 (12)kV x 3C x 6 Sqmm | 1070 |  | 2 | H1IK | 16 | 16 | [20 empty] | 1 | 1 |  |  |  |  | 1 | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | LV LOADS | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 1409-TFD-2-0007 (1409-SWG-4-0004) | 11kV MV Switchgear-3 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 7 (LV SWITCHGEAR-4 FOR SEA WATER TREATMENT) | SEA WATER TREATMENT BUILDING | A | POWER | 1317.42 | kW | 3Ph | 11000 | 0.84225 | 0.9 | 91.2217 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 26 | 10 | 5 | 8 | 5 | 60 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.023556 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 60 |  | 2 | H1 | 62 | 62 | [20 empty] | 1 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 1409-TFD-2-0008 (1409-SWG-4-0004) | 11kV MV Switchgear-3 | OUTGOING FEEDER FOR 11/0.42kV TRANSFORMER - 8 (LV SWITCHGEAR-4 FOR SEA WATER TREATMENT) | SEA WATER TREATMENT BUILDING | B | POWER | 1317.42 | kW | 3Ph | 11000 | 0.84225 | 0.9 | 91.2217 | 0 | 0.00 | 31.5 | 0.16 | 134.0426 | AIR | 3C | 150 | 3C X 150 | 3C X 150 | 6/10(12) | 309 | 0.265 | 0.093 | 26 | 15 | 5 | 8 | 6 | 60 | 0.82 | 0.73 | NA | NA | NA | 0.5986 | 184.9674 | 1 | YES | 0.023556 | YES | NA | NA | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 1R x 6/10 (12)kV x 3C x 150 Sqmm | 60 |  | 2 | H1 | 62 | 62 | [20 empty] | 1 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 1409-SWG-2-0003 | 11kV MV Switchgear-1 | 11kV SWITCHGEAR-3 INCOMER 1 | MAIN SUBSTATION BUILDING | A | POWER | 3036.33 | kW | 3Ph | 11000 | 0.85573 | 0.94463 | 197.1563 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 1409-SWG-2-0003 | 11kV MV Switchgear-1 | 11kV SWITCHGEAR-3 INCOMER 2 | MAIN SUBSTATION BUILDING | B | POWER | 3036.33 | kW | 3Ph | 11000 | 0.85573 | 0.94463 | 197.1563 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[49 empty] | 24990 |  | 128 | [73 empty] | 0 | 1979 | 0 | 0 | 1550 | 1336 | 0 | 0 | 0 | 1336 | 0 | 772 | 618 | 464 | 263 | 139 | 0 | 564 | 564 | 132 | 490 | 666 | 0 | 0 | 124 | 308 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 600 | 0 | 3.958 | 0 | 0 | 3.1 | 2.672 | 0 | 0 | 0 | 2.672 | 0 | 1.544 | 1.236 | 0.928 | 0.526 | 0.278 | 0 | 1.128 | 1.128 | 0.264 | 0.98 | 1.332 | 0 | 0 | 0.248 | 0.616 | 0.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.858 | 0 | 0.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 4 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 3 | 0 | 2 | 2 | 1 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 2 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 750 | 0 | 3.1664 | 0 | 0 | 2.48 | 2.1376 | 0 | 0 | 0 | 2.1376 | 0 | 1.2352 | 0.9888 | 0.7424 | 0.4208 | 0.2224 | 0 | 0.9024 | 0.9024 | 0.2112 | 0.784 | 1.0656 | 0 | 0 | 0.1984 | 0.4928 | 0.3744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6864 | 0 | 0.6864 | 0 | 0 | 0 | 0 | 0 | 0 | 0.488 | 0.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 4 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 900 | 0 | 0.0064 | 0 | 0 | 0.0064 | 0.0048 | 0 | 0 | 0 | 0.0048 | 0 | 0.0032 | 0.0032 | 0.0016 | 0.0016 | 0.0016 | 0 | 0.0032 | 0.0032 | 0.0016 | 0.0016 | 0.0032 | 0 | 0 | 0.0016 | 0.0016 | 0.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016 | 0 | 0.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016 | 0.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[33 empty] | 565 | 1 | 1
[33 empty] | 547 | 1 | 1
[33 empty] | 566 | 1 | 1
[33 empty] | 554 | 1 | 1
[33 empty] | 1065 | 1 | 2
[33 empty] | 1065 | 1 | 2
[33 empty] | 1065 | 1 | 2
10

## Sheet2 (hidden)
24 nos | 88 | 24 |  | 2112 | 2534.4 |  | 2 nos
7 nos | 86 | 7 |  | 602 | 722.4 |  | 2 nos
8 nos | 88 | 8 |  | 704 | 844.8 |  | 2 nos
7 nos | 86 | 7 |  | 602 | 722.4 |  | 2 nos
Electrolyzer Area Cable Tray requirement
Main entry
| 33kV | 5.428 | Cable Trench | Ladded | 600mm | 6
| LV | 1 | Cable Trench | Ladded | 600mm | 1
| Control | 1 | Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Cable Trench | Perforated | 600mm | 2
Package-1 & Electrolyzer building
| 33kV | 2.612 | Cable Trench | Ladded | 600mm | 3
| LV | 1 | Cable Trench | Ladded | 600mm | 1
| Control | 1 | Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Cable Trench | Perforated | 600mm | 2
Package-2 & 3
| 33kV | 2.816 | Cable Trench | Ladded | 600mm | 3
| LV | 1 | Cable Trench | Ladded | 600mm | 1
| Control | 1 | Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Cable Trench | Perforated | 600mm | 2
Package- 3
| 33kV | 1.408 | Pipe Rack & Cable Trench | Ladded | 600mm | 2
| LV | 1 | Pipe Rack & Cable Trench | Ladded | 600mm | 1
| Control | 1 | Pipe Rack & Cable Trench | Perforated | 600mm | 1
| I&C | 2 | Pipe Rack & Cable Trench | Perforated | 600mm | 2

## LV Cable sizing_SS-1
LV POWER CABLE SIZING
Sl. No |  |  | LOAD | [12 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  | CABLE DATA | [14 empty] | DERATING FACTOR | [5 empty] | CURRENT CARRYING CAPACITY |  |  | RUNNING CONDITION VOLTAGE DROP |  | MOTOR STARTING VOLTAGE DROP |  | Selected Cable Size
| Tag No. | From | Description | Equipment Location | Bus | Type of feeder | Rated power | UNIT (kW / kVa) | 3Phase / 1Phase | Rated Voltage (V) | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard (kA) | Short circuit current withstand duration (sec) | Minimum size required for Short circuit withstand capacity (Sq.mm) | Installation | No. of Cores | Size in (Sq.mm) | Cable size | Cable size With (PE) Core | Cable Voltage (kV) | Current Rating of the Cable (A) | Cable resistance at 90°C (Ohm / Ph / km) | Cable reactance at 50Hz (Ohm / Ph / km) | Cable Length with in Electrical Building (m) | Cable Length from Electrical Building to Equipment (m) | Cable length Riser & Dropper (m) | Cable length both side dropping & Termination (m) | Spare 10% | Cable length for each run (m) | Ambient temperature (K1) | Grouping factor (K2) | Ground temperature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | Derated current carrying capacity (A) | No. of Runs | Derated current > Rated current | % VOLTAGE DROP DURING RUNNING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT (YES/NO) | % VOLTAGE DROP DURING STARTING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT DURING STARTING CONDITION (YES/NO) | Selected cable size | Selected cable size | Total Cable Length in meters | Remarks | No. of End Termination | Cable Route(Sections) | Dia of the conductor(mm) | Total Dia of the conductor(mm) | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | I.A | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | T.A | T1.A | U |  | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | I.A | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | T.A | T1.A | U
MAIN SUBSTATION
PMCC-1
X | 1401-PM104A | PMCC-1 | BFW PUMP | AMMONIA PLANT | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.957 | 133.083 | 798.4979 | 0.2 | 65 | 0 | 0 | AIR | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 29 | 263 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 185 Sqmm | 1R x 0.6/1kV x 3C x 185+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | 1401-PM104B | PMCC-1 | SPARE BFW PUMP | AMMONIA PLANT | B | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.957 | 133.083 | 798.4979 | 0.2 | 65 | 0 | 0 | AIR | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 38 | 263 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 185 Sqmm | 1R x 0.6/1kV x 3C x 185+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | 1401-PM112A | PMCC-1 | CONDENSATE PUMP FOR 1401-C-301 | AMMONIA PLANT | A | MOTOR | 9.3 | kW | 3Ph | 400 | 0.79 | 0.906 | 18.7551 | 112.5307 | 0.2 | 65 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 29 | 309 | 38 | 8 | 39 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | 1401-PM112B | PMCC-1 | CONDENSATE PUMP FOR 1401-C-301 | AMMONIA PLANT | B | MOTOR | 9.3 | kW | 3Ph | 400 | 0.79 | 0.906 | 18.7551 | 112.5307 | 0.2 | 65 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 309 | 38 | 8 | 40 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
1 | 1401-PM116A | PMCC-1 | CONDENSATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 315 | 38 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.72016 | YES | 1.258 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 429 |  | 2 | ACDEE1E2E3E4E5 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1401-PM107A | PMCC-1 | PH CONTROL INJECTION SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 266 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.6463 | YES | 1.129 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 385 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1401-PM108A | PMCC-1 | PHOSPHATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 284 | 38 | 8 | 36 | 395 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.66308 | YES | 1.1583 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 395 |  | 2 | ACDEE1E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 |  | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1401-PM106A | PMCC-1 | OXYGEN SCAVENGER SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.65133 | YES | 1.1378 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 388 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1401-PM116B | PMCC-1 | CONDENSATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 315 | 38 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.72016 | YES | 1.258 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 429 |  | 2 | ACDEE1E2E3E4E5 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1401-PM107B | PMCC-1 | PH CONTROL INJECTION SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 266 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.6463 | YES | 1.129 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 385 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1401-PM108B | PMCC-1 | PHOSPHATE INJECTION SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 284 | 38 | 8 | 36 | 395 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.66308 | YES | 1.1583 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 395 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1401-PM106B | PMCC-1 | OXYGEN SCAVENGER SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.88678 | 5.3207 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 268 | 38 | 8 | 35 | 378 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.63454 | YES | 1.1085 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 378 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1401-LFA108 | PMCC-1 | PHOSPHATE INJECTION SYSTEM PUMP | AMMONIA PLANT | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.73 | 0.825 | 1.7975 | 10.7852 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 284 | 38 | 8 | 37 | 405 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.3781 | YES | 2.4073 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 405 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1401-LFA106 | PMCC-1 | OXYGEN SCAVENGER SYSTEM PUMP | AMMONIA PLANT | A | MOTOR | 0.75 | kW | 3Ph | 400 | 0.73 | 0.825 | 1.7975 | 10.7852 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 268 | 38 | 8 | 35 | 378 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.2862 | YES | 2.2469 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 378 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 |  | PMCC-1 | ELECTRICAL STROKE SETTING DEVICE FOR STEAM CONDENSATE INJECTION UNIT | AMMONIA PLANT | A | MOTOR | 0.01 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.072193 | 0.43316 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 268 | 38 | 8 | 35 | 378 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.089841 | YES | 0.15694 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 378 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 |  | PMCC-1 | STANDBY ELECTRICAL STROKE SETTING DEVICE FOR STEAM CONDENSATE INJECTION UNIT | AMMONIA PLANT | B | MOTOR | 0.01 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.072193 | 0.43316 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.092217 | YES | 0.16109 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 388 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 1411-JM001A | PMCC-1 | INSTRUMENT AIR COMPRESSOR -A | INSTRUMENT AIR COMPRESSOR AREA | A | MOTOR | 160 | kW | 3Ph | 400 | 0.86 | 0.964 | 278.5715 | 1671.4288 | 0.2 | 65 | 0 | 0 | AIR | 3C | 300 | 3C X 300 | 3C X 300+PE | 0.6/1.0 | 459 | 0.128 | 0.0711 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.1009 | YES | 8.2047 | YES | 2R x 0.6/1kV x 3C x 300 Sqmm | 2R x 0.6/1kV x 3C x 300+PE Sqmm | 476 |  | 4 | D3LMM1 | 53 | 106 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 1411-JM001A | PMCC-1 | INSTRUMENT AIR COMPRESSOR -A-SPACE HEATER | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.5655 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 238 |  | 2 | D3LMM1 | 14 | 14 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 1411-JM001B | PMCC-1 | INSTRUMENT AIR COMPRESSOR- B | INSTRUMENT AIR COMPRESSOR AREA | B | MOTOR | 160 | kW | 3Ph | 400 | 0.86 | 0.964 | 278.5715 | 1671.4288 | 0.2 | 65 | 0 | 0 | AIR | 3C | 300 | 3C X 300 | 3C X 300+PE | 0.6/1.0 | 459 | 0.128 | 0.0711 | 28 | 157 | 22 | 8 | 22 | 237 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.0921 | YES | 8.1702 | YES | 2R x 0.6/1kV x 3C x 300 Sqmm | 2R x 0.6/1kV x 3C x 300+PE Sqmm | 474 |  | 4 | D3LMM1 | 53 | 106 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 1411-JM001B | PMCC-1 | INSTRUMENT AIR COMPRESSOR- B-SPACE HEATER | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 28 | 157 | 22 | 8 | 22 | 237 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.5589 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 237 |  | 2 | D3LMM1 | 14 | 14 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 1411-JM001C | PMCC-1 | INSTRUMENT AIR COMPRESSOR- C | INSTRUMENT AIR COMPRESSOR AREA | A | MOTOR | 160 | kW | 3Ph | 400 | 0.86 | 0.964 | 278.5715 | 1671.4288 | 0.2 | 65 | 0 | 0 | AIR | 3C | 300 | 3C X 300 | 3C X 300+PE | 0.6/1.0 | 459 | 0.128 | 0.0711 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.1009 | YES | 8.2047 | YES | 2R x 0.6/1kV x 3C x 300 Sqmm | 2R x 0.6/1kV x 3C x 300+PE Sqmm | 476 |  | 4 | D3LMM1 | 53 | 106 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 1411-JM001C | PMCC-1 | INSTRUMENT AIR COMPRESSOR- C-SPACE HEATER | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 29 | 157 | 22 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.5655 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 238 |  | 2 | D3LMM1 | 14 | 14 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 1411-D001A | PMCC-1 | INSTRUMENT AIR DRYER | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.89376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.5018 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 256 |  | 2 | D3LMM1 | 16 | 16 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 1411-D001B | PMCC-1 | STANDBY INSTRUMENT AIR DRYER | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 0.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.89376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 162 | 22 | 8 | 22 | 242 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.47436 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 242 |  | 2 | D3LMM1 | 16 | 16 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 1411-V001 | PMCC-1 | ADT for Air receciver 25M³ | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.03 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.21658 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 162 | 22 | 8 | 22 | 242 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.17255 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 242 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 1411-V002A | PMCC-1 | ADT for Air receciver 60M³ | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 0.03 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.21658 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.18253 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 256 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 1411-V002B | PMCC-1 | ADT for Air receciver 60M³ | INSTRUMENT AIR COMPRESSOR AREA | A | POWER | 0.03 | kW | 1Ph | 230 | 0.73 | 0.825 | 0.21658 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 162 | 22 | 8 | 22 | 242 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.17255 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 242 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 1417-P-001A | PMCC-1 | Electrolyte (KOH) Drain pump | INSTRUMENT AIR COMPRESSOR AREA | B | MOTOR | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 32.1753 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.019 | YES | 3.1257 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 256 |  | 2 | D3LMM1 | 16 | 16 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 1417-P-001B | PMCC-1 | Electrolyte (KOH) Drain pump | INSTRUMENT AIR COMPRESSOR AREA | B | MOTOR | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 32.1753 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.019 | YES | 3.1257 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 256 |  | 2 | D3LMM1 | 16 | 16 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | MASTER PLC | INSTRUMENT AIR COMPRESSOR AREA | B | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 162 | 22 | 8 | 24 | 256 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.0072 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 256 |  | 2 | D3LMM1 | 16 | 16 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | ASU PACKAGE (1404-PK001) | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | ASU-SELF CLEANING FILTER A | AIR SEPARATION UNIT | B | MOTOR | 0.1 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.23967 | 1.438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 103 | 22 | 8 | 17 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | ASU-SELF CLEANING FILTER B | AIR SEPARATION UNIT | A | MOTOR | 0.1 | kW | 3Ph | 400 | 0.73 | 0.825 | 0.23967 | 1.438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 40 | 103 | 22 | 8 | 18 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | ASU-PRECOOLING SYSTEM A | AIR SEPARATION UNIT | B | MOTOR | 78 | kW | 3Ph | 400 | 0.85 | 0.957 | 138.4063 | 830.4378 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 33 | 133 | 22 | 8 | 20 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 150 Sqmm | 1R x 0.6/1kV x 3C x 150+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | ASU-PRECOOLING SYSTEM B | AIR SEPARATION UNIT | B | MOTOR | 78 | kW | 3Ph | 400 | 0.85 | 0.957 | 138.4063 | 830.4378 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 33 | 133 | 22 | 8 | 20 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 150 Sqmm | 1R x 0.6/1kV x 3C x 150+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | EXPANDER ELECTRIC HEATER | AIR SEPARATION UNIT | B | POWER | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 158 | 22 | 8 | 23 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | STEAM TURBINE GENERATOR | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | - | PMCC-1 | STG 1401-JT/JC301 - FEEDER (SPARE) | AMMONIA PLANT | B | POWER | 86.54 | kW | 3Ph | 400 | 0.85 | 0.95 | 154.6915 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 300 | 3.5C X 300 | 3.5C X 300 | 0.6/1.0 | 459 | 0.128 | 0.0711 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.165 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 884 |  | 4 | ACDEE1E2E3E4E5 | 64 | 128 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 128 | 0 | 0 | 128 | 128 | 0 | 0 | 0 | 128 | 0 | 128 | 128 | 128 | 128 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | - | PMCC-1 | STG 1401-JT/JC301 - FEEDER (SPARE) | AMMONIA PLANT | A | POWER | 86.54 | kW | 3Ph | 400 | 0.85 | 0.95 | 154.6915 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 300 | 3.5C X 300 | 3.5C X 300 | 0.6/1.0 | 459 | 0.128 | 0.0711 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 2.2091 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 902 |  | 4 | ACDEE1E2E3E4E5 | 64 | 128 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 128 | 0 | 0 | 128 | 128 | 0 | 0 | 0 | 128 | 0 | 128 | 128 | 128 | 128 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 1401-P-1601 | PMCC-1 | Lubricating oil pump 1 | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 235.9519 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 28 | 335 | 38 | 8 | 41 | 450 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 2 | YES | 1.4834 | YES | 3.5383 | YES | 2R x 0.6/1kV x 3C x 95 Sqmm | 2R x 0.6/1kV x 3C x 95+PE Sqmm | 900 |  | 4 | ACDEE1E2E3E4E5 | 33 | 66 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 66 | 0 | 0 | 66 | 66 | 0 | 0 | 0 | 66 | 0 | 66 | 66 | 66 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | - | PMCC-1 | Lubricating oil pump 1-Space Heater | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 28 | 335 | 38 | 8 | 41 | 450 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.88798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 450 |  | 2 | ACDEE1E2E3E4E5 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 1401-P-1602 | PMCC-1 | Lubricating oil pump 2 | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 235.9519 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 2 | YES | 1.457 | YES | 3.4754 | YES | 2R x 0.6/1kV x 3C x 95 Sqmm | 2R x 0.6/1kV x 3C x 95+PE Sqmm | 884 |  | 4 | ACDEE1E2E3E4E5 | 33 | 66 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 66 | 0 | 0 | 66 | 66 | 0 | 0 | 0 | 66 | 0 | 66 | 66 | 66 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | - | PMCC-1 | Lubricating oil pump 2-Space Heater | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.87219 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 442 |  | 2 | ACDEE1E2E3E4E5 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | - | PMCC-1 | Generator heater | AMMONIA PLANT | A | POWER | 0.4 | kW | 1Ph | 230 | 0.85 | 0.95 | 2.1537 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.4845 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 451 |  | 2 | ACDEE1E2E3E4E5 | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 1401-PM-1604A | PMCC-1 | GSC Blower | AMMONIA PLANT | B | MOTOR | 3.7 | kW | 3Ph | 400 | 0.85 | 0.95 | 6.6138 | 39.6828 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.6797 | YES | 4.3128 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 442 |  | 2 | ACDEE1E2E3E4E5 | 19 | 19 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 19 | 0 | 0 | 19 | 19 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 1401-PM-1604 | PMCC-1 | Oil Vapour Extractor | AMMONIA PLANT | A | MOTOR | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 16.0876 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.6521 | YES | 3.9988 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 451 |  | 2 | ACDEE1E2E3E4E5 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 1401-HT-1601 | PMCC-1 | Heater for oil tank | AMMONIA PLANT | B | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 335 | 38 | 8 | 41 | 437 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.4996 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 437 |  | 2 | ACDEE1E2E3E4E5 | 27 | 27 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 27 | 0 | 27 | 27 | 27 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 1401-PM112A | PMCC-1 | Condensate Extraction Pump 1 | AMMONIA PLANT | A | MOTOR | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 80.4382 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 335 | 38 | 8 | 41 | 451 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5797 | YES | 4.7094 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 451 |  | 2 | ACDEE1E2E3E4E5 | 23 | 23 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 23 | 0 | 0 | 23 | 23 | 0 | 0 | 0 | 23 | 0 | 23 | 23 | 23 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 1401-PM112B | PMCC-1 | Condensate Extraction Pump 2 | AMMONIA PLANT | B | MOTOR | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 80.4382 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5282 | YES | 4.6154 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 442 |  | 2 | ACDEE1E2E3E4E5 | 23 | 23 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 23 | 0 | 0 | 23 | 23 | 0 | 0 | 0 | 23 | 0 | 23 | 23 | 23 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | - | PMCC-1 | Barring Gear Motor | AMMONIA PLANT | B | MOTOR | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 80.4382 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5282 | YES | 4.6154 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 442 |  | 2 | ACDEE1E2E3E4E5 | 23 | 23 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 23 | 0 | 0 | 23 | 23 | 0 | 0 | 0 | 23 | 0 | 23 | 23 | 23 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | - | PMCC-1 | GVC motor | AMMONIA PLANT | B | MOTOR | 5.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 9.8313 | 58.988 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 335 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.5439 | YES | 4.3799 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 442 |  | 2 | ACDEE1E2E3E4E5 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Synthesis Gas compressor 1401-J-103 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 1401-HT103A | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J103 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 286 | 38 | 8 | 37 | 398 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.0872 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 398 |  | 2 | ACDEE1E2E3 | 39 | 39 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 39 | 0 | 0 | 39 | 39 | 0 | 0 | 0 | 39 | 0 | 39 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | - | PMCC-1 | UCP FOR 1401-J103 (UPS 230 V)(REDUNDANT SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | - | PMCC-1 | UCP FOR 1401-J103 (UPS 230 V)(MAIN SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | - | PMCC-1 | LUBE OIL ELECTRIC HEATER B for 1401-J103 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 287 | 38 | 8 | 37 | 399 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.0925 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 399 |  | 2 | ACDEE1E2E3 | 39 | 39 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 39 | 0 | 0 | 39 | 39 | 0 | 0 | 0 | 39 | 0 | 39 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | - | PMCC-1 | MOTOR SPACE HEATER FOR 1401-J103(230V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 297 | 38 | 8 | 37 | 400 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1928 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 400 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | MISCLENEOUS LOADS FOR SPARES | AMMONIA PLANT | A | POWER | 55 | kW | 3Ph | 400 | 0.85 | 0.95 | 98.3133 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 296 | 38 | 8 | 38 | 409 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 2 | YES | 11.77 | NO | NA | NA | 2R x 0.6/1kV x 3.5C x 25 Sqmm | 2R x 0.6/1kV x 3.5C x 25 Sqmm | 818 |  | 4 | ACDEE1E2E3 | 25 | 50 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 50 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 50 | 0 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | LUBE OIL ELECTRIC HEATER B for 1401-J105 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 304 | 38 | 8 | 38 | 417 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 7.6365 | NO | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | MOTOR SPACE HEATER FOR 1401-J105 | AMMONIA PLANT | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 25 | 4C X 25 | 4C X 25 | 0.6/1.0 | #N/A | #N/A | #N/A | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A | #N/A | #N/A | #N/A | #N/A | NA | NA | #N/A | #N/A | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
43 | 0 | PMCC-1 | SPACE HEATER FOR SPARE LUBE OIL PUMP FOR 1401-J103 (230 V) | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 286 | 38 | 8 | 37 | 398 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.13091 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 398 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 0 | PMCC-1 | SPACE HEATER FOR MAIN LUBE OIL PUMP FOR1401-J103 (230 V) | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 287 | 38 | 8 | 36 | 389 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.12795 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 389 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 1401-CM113 | PMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J103 | AMMONIA PLANT | A | MOTOR | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 42.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 286 | 38 | 8 | 37 | 398 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.6086 | YES | 4.1984 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 398 |  | 2 | ACDEE1E2E3 | 19 | 19 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 19 | 0 | 0 | 19 | 19 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 0 | PMCC-1 | UCP LIGHTNING FOR 1401-J103 (NON-UPS 230 V) | CENTRAL CONTROL BUILDING | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.68524 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 125 |  | 2 | AB | 21 | 21 |  | 1 | 1 | [67 empty] | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 1401-CM106 | PMCC-1 | TURNING GEAR MOTOR FOR GEAR BOX | AMMONIA PLANT | A | MOTOR | 1.1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.9663 | 11.7976 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 297 | 38 | 8 | 38 | 410 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.7681 | YES | 2.6658 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 410 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 1401-HT105 | PMCC-1 | PRIMARY SEAL GAS HEATER (LP) | AIR SEPARATION UNIT | B | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 142 | 38 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.8061 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 229 |  | 2 | AC | 18 | 18 |  | 1 |  |  | 1 | [65 empty] | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 1401-HT106 | PMCC-1 | PRIMARY SEAL GAS HEATER (MP) | AIR SEPARATION UNIT | A | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.9581 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 239 |  | 2 | AC | 21 | 21 |  | 1 |  |  | 1 | [65 empty] | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 1401-HT107 | PMCC-1 | PRIMARY SEAL GAS HEATER (HP) | AIR SEPARATION UNIT | B | POWER | 8 | kW | 3Ph | 400 | 0.85 | 0.95 | 14.3001 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 142 | 38 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9171 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 229 |  | 2 | AC | 25 | 25 |  | 1 |  |  | 1 | [65 empty] | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0 | PMCC-1 | MAIN VFD AUX. POWER SUPPLY | AIR SEPARATION UNIT | A | POWER | 28 | kW | 3Ph | 400 | 0.85 | 0.95 | 50.0504 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.0054 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 239 |  | 2 | AC | 39 | 39 |  | 1 |  |  | 1 | [65 empty] | 0 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | LUBE OIL PURIFIER - SEPARATION CYLINDER MOTOR | AMMONIA PLANT | A | MOTOR | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 32.1753 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 286 | 38 | 8 | 37 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.28254 | YES | 0.48645 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | LUBE OIL PURIFIER - BOOSTER WATER PUMP | AMMONIA PLANT | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.3406 | 8.0438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 286 | 38 | 8 | 36 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.070636 | YES | 0.12161 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | LUBE OIL PURIFIER - OIL SUPPLY PUMP | AMMONIA PLANT | A | MOTOR | 0.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.3406 | 8.0438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 286 | 38 | 8 | 37 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.070636 | YES | 0.12161 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | LUBE OIL PURIFIER - SLAG DISCHARGE PUMP | AMMONIA PLANT | B | MOTOR | 0.55 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.98313 | 5.8988 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 286 | 38 | 8 | 36 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.0518 | YES | 0.089183 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 90 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | LUBE OIL PURIFIER - ELECTRICAL PANEL | CENTRAL CONTROL BUILDING | A | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 25 | 4C X 25 | 4C X 25 | 0.6/1.0 | #N/A | #N/A | #N/A | 29 | 80 | 5 | 8 | 13 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A | #N/A | #N/A | #N/A | #N/A | NA | NA | #N/A | #N/A | #N/A |  | #N/A | AB | #N/A | #N/A |  | 1 | 1 | [67 empty] | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | LUBE OIL PURIFIER - PLC PANEL | CENTRAL CONTROL BUILDING | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 25 | 4C X 25 | 4C X 25 | 0.6/1.0 | #N/A | #N/A | #N/A | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A | #N/A | #N/A | #N/A | #N/A | NA | NA | #N/A | #N/A | #N/A |  | #N/A | AB | #N/A | #N/A |  | 1 | 1 | [67 empty] | 0 | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | AMMONIA REFRIGERATION COMPRESSOR 1401-J-105 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 1401-HT105A | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J105 | AMMONIA PLANT | A | POWER | 13 | kW | 3Ph | 400 | 0.85 | 0.95 | 23.2377 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 304 | 38 | 8 | 38 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.2244 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 90 |  | 2 | ACDEE1E2E3E4 | 25 | 25 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 25 | 0 | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | - | PMCC-1 | UCP FOR 1401-J105 (UPS 230 V)(REDUNDANT SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90 |  | 2 | AB | 21 | 21 |  | 1 | 1 | [67 empty] | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | - | PMCC-1 | UCP FOR 1401-J105 (UPS 230 V)(MAIN SUPPLY) | CENTRAL CONTROL BUILDING | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.95 | 26.9215 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 80 | 5 | 8 | 12 | 90 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4669 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 90 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | - | PMCC-1 | UCP LIGHTNING FOR 1401-J105 (NON-UPS 230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.8592 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 135 |  | 2 | AB | 16 | 16 |  | 1 | 1 | [67 empty] | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 1401-HT105B | PMCC-1 | LUBE OIL ELECTRIC HEATER B for 1401-J105 | AMMONIA PLANT | B | POWER | 13 | kW | 3Ph | 400 | 0.85 | 0.95 | 23.2377 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 20 | 304 | 38 | 8 | 37 | 407 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 2.136 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 407 |  | 2 | ACDEE1E2E3E4 | 36 | 36 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 36 | 0 | 0 | 36 | 36 | 0 | 0 | 0 | 36 | 0 | 36 | 36 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 1401-HT206 | PMCC-1 | MOTOR SPACE HEATER FOR 1401-J105 (230 V) | AMMONIA PLANT | A | POWER | 0.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3074 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 314 | 38 | 8 | 39 | 428 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.877 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 428 |  | 2 | ACDEE1E2E3E4 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 1401-CM107 | PMCC-1 | TURNING GEAR MOTOR FOR GEAR BOX | AMMONIA PLANT | B | MOTOR | 1.1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.9663 | 11.7976 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 309 | 38 | 8 | 38 | 413 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.781 | YES | 2.6853 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 413 |  | 2 | ACDEE1E2E3E4 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 1401-HT207 | PMCC-1 | PRIMARY SEAL GAS HEATER (LP) | AIR SEPARATION UNIT | A | POWER | 6 | kW | 3Ph | 400 | 0.85 | 0.95 | 10.7251 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.5006 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 239 |  | 2 | AC | 25 | 25 |  | 1 |  |  | 1 | [65 empty] | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 1401-HT108 | PMCC-1 | PRIMARY SEAL GAS HEATER (HP) | AIR SEPARATION UNIT | B | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 142 | 38 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.8061 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 229 |  | 2 | AC | 18 | 18 |  | 1 |  |  | 1 | [65 empty] | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | - | PMCC-1 | MAIN VFD AUX. POWER SUPPLY | AIR SEPARATION UNIT | A | POWER | 16 | kW | 3Ph | 400 | 0.85 | 0.95 | 28.6002 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.1865 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 239 |  | 2 | AC | 30 | 30 |  | 1 |  |  | 1 | [65 empty] | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 1401-PM107 | PMCC-1 | LUBE OIL CONDITIONER OIL PUMP MOTOR | AIR SEPARATION UNIT | A | MOTOR | 5.25 | kW | 3Ph | 400 | 0.85 | 0.95 | 9.3845 | 56.3067 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.056 | YES | 3.309 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 239 |  | 2 | AC | 19 | 19 |  | 1 |  |  | 1 | [65 empty] | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N2 Compressor | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | - | PMCC-1 | SPACE HEATER FOR 1401-CM201 (230V) | AMMONIA PLANT | A | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 283 | 38 | 8 | 36 | 394 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1599 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 394 |  | 2 | ACDEE1E2E3 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 1401-DM210 | PMCC-1 | OIL MIST ELIMINATOR MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.3406 | 8.0438 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 284 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.132 | YES | 1.7068 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 385 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 1401-PKM210A | PMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | A | MOTOR | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 16.0876 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 285 | 38 | 8 | 36 | 396 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.3287 | YES | 3.5111 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 396 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 1401-PKM210B | PMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 16.0876 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 285 | 38 | 8 | 36 | 387 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.2757 | YES | 3.4313 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 387 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 1401-B210 | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | A | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 287 | 38 | 8 | 37 | 399 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.5642 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 399 |  | 2 | ACDEE1E2E3 | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 1401-B211 | PMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 287 | 38 | 8 | 36 | 389 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.525 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 389 |  | 2 | ACDEE1E2E3 | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 401-PJB-1401 | PMCC-1 | Acoustic Enclosure lighting JB (230V) (NON-UPS Supply) | CENTRAL CONTROL BUILDING | B | POWER | 0.6 | kW | 1Ph | 230 | 0.85 | 0.95 | 3.2306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.6758 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 136 |  | 2 | ACDEE1E2E3 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 401-PLC-1401 | PMCC-1 | Package PLC Panel (230V)(NON-UPS Supply) | CENTRAL CONTROL BUILDING | B | POWER | 0.9 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.8459 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.6857 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 136 |  | 2 | AB | 16 | 16 |  | 1 | 1 | [67 empty] | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 401-MMS-1401 | PMCC-1 | MMS Panel (230V) (NON-UPS Supply) | CENTRAL CONTROL BUILDING | A | POWER | 1.1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.9227 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 85 | 10 | 8 | 14 | 146 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.2118 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 146 |  | 2 | AB | 16 | 16 |  | 1 | 1 | [67 empty] | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 401-PLC-1401 | PMCC-1 | Package PLC Panel (UPS supply) (230V) | CENTRAL CONTROL BUILDING | B | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 136 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 401-MMS-1401 | PMCC-1 | MMS Panel (UPS supply) (230V) | CENTRAL CONTROL BUILDING | A | POWER | 2.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 11.8455 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 85 | 10 | 8 | 14 | 146 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.7608 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 146 |  | 2 | AB | 21 | 21 |  | 1 | 1 | [67 empty] | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | - | PMCC-1 | Laptop (UPS supply) (230V) | CENTRAL CONTROL BUILDING | B | POWER | 0.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 2.6922 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 20 | 85 | 10 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.3965 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 136 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Auxiliary H2 Compressor (1401-J-202A/B) | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-1 | UCP CABINET FOR 1401-J203A | AMMONIA PLANT | B | MOTOR | 6 | kW | 3Ph | 400 | 0.82 | 0.896 | 11.7875 | 70.725 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 237 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | REMOTE I/O CABINET FOR 1401-J203A | AMMONIA PLANT | A | MOTOR | 4 | kW | 3Ph | 400 | 0.79 | 0.886 | 8.2488 | 49.4929 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | MMS CABINET FOR 1401-J203A | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.75 | 0.853 | 4.5124 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | UCP CABINET FOR 1401-J203B | AMMONIA PLANT | B | POWER | 6 | kW | 3Ph | 400 | 0.85 | 0.95 | 10.7251 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | REMOTE I/O CABINET FOR1401-J203B | AMMONIA PLANT | B | MOTOR | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 42.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | PMCC-1 | MMS CABINET FOR 1401-J203B | AMMONIA PLANT | B | POWER | 1.6 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.86 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
74 | 1401-H202A | PMCC-1 | FRAME OIL HEATER FOR 1401-J202A | AMMONIA PLANT | A | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 237 | 38 | 8 | 32 | 344 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.9677 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 344 |  | 2 | ACDEE1E2 | 27 | 27 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 27 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202A (240 V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 267 | 38 | 8 | 34 | 367 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0119 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 367 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 269 | 38 | 8 | 35 | 379 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.9928 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 379 |  | 2 | ACDEE1E2 | 18 | 18 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 18 | 0 | 0 | 18 | 18 | 0 | 0 | 0 | 18 | 0 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 1401-H202B | PMCC-1 | FRAME OIL HEATER FOR 1401-J202B | AMMONIA PLANT | A | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 269 | 38 | 8 | 35 | 379 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.1679 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 379 |  | 2 | ACDEE1E2 | 27 | 27 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 27 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202B (240 V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 270 | 38 | 8 | 34 | 370 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0283 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 370 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 269 | 38 | 8 | 35 | 379 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.9928 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 379 |  | 2 | ACDEE1E2 | 18 | 18 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 18 | 0 | 0 | 18 | 18 | 0 | 0 | 0 | 18 | 0 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Auxiliary H2 Compressor (1401-J-203A/B) | [16 empty] | 3C | [104 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 1401-H203A | PMCC-1 | FRAME OIL HEATER FOR 1401-J203A | AMMONIA PLANT | A | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 247 | 38 | 8 | 33 | 355 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.0306 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 355 |  | 2 | ACDEE1E2 | 27 | 27 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 27 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203A (240 V) | AMMONIA PLANT | B | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 256 | 38 | 8 | 33 | 355 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9461 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 355 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 257 | 38 | 8 | 34 | 366 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.9244 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 366 |  | 2 | ACDEE1E2 | 18 | 18 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 18 | 0 | 0 | 18 | 18 | 0 | 0 | 0 | 18 | 0 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | B | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 80 | 5 | 8 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1459 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 125 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | B | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 80 | 5 | 8 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1459 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 125 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 1401-B203C | PMCC-1 | WATER TANK HEATER FOR 1401-J203A/B & 1401-J202A/B | AMMONIA PLANT | A | POWER | 70 | kW | 3Ph | 400 | 0.85 | 0.95 | 125.126 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 29 | 247 | 38 | 8 | 33 | 350 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 2.4933 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 700 |  | 4 | ACDEE1E2 | 48 | 96 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 96 | 0 | 0 | 96 | 96 | 0 | 0 | 0 | 96 | 0 | 96 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 1401-H203B | PMCC-1 | FRAME OIL HEATER FOR 1401-J203A | AMMONIA PLANT | B | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 248 | 38 | 8 | 32 | 346 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.9791 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 346 |  | 2 | ACDEE1E2 | 27 | 27 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 27 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | - | PMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203 B (240 V) | AMMONIA PLANT | A | POWER | 1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.3843 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 262 | 38 | 8 | 34 | 371 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0338 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 371 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | - | PMCC-1 | Excitation Panel Main supply | AMMONIA PLANT | B | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 20 | 263 | 38 | 8 | 33 | 362 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.1863 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 362 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | - | PMCC-1 | Excitation Panel Aux supply (240 V) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | - | PMCC-1 | Excitation Panel Aux supply (UPS) (240 V) | CENTRAL CONTROL BUILDING | B | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | - | PMCC-1 | Excitation Panel control supply (24 VDC / 110 VDC) | CENTRAL CONTROL BUILDING | A | POWER | 2 | kW | 1Ph | 230 | 0.85 | 0.95 | 10.7686 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 80 | 5 | 8 | 13 | 135 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3176 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 135 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other Load | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 1421-MLDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR MLDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 85 | kW | 3Ph | 400 | 0.85 | 0.95 | 151.9387 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 34 | 0 | 5 | 8 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0.89963 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 52 |  | 2 |  | 48 | 48 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 1421-MLDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR MLDB-1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 85 | kW | 3Ph | 400 | 0.85 | 0.95 | 151.9387 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 18 | 0 | 5 | 8 | 4 | 35 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 0.60552 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 35 |  | 2 |  | 48 | 48 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 1421-WDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR WDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 60 | kW | 3Ph | 400 | 0.85 | 0.95 | 107.2509 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 34 | 0 | 5 | 8 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 0.93498 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 52 |  | 2 |  | 39 | 39 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 1421-PDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR PDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 363.56 | kW | 3Ph | 400 | 0.85 | 0.951 | 649.1854 | 0 | 0.00 | 65 | 0 | 0 | AIR | 1C | 500 | 1C X 500 | 1C X 500 | 0.6/1.0 | 704 | 0.0774 | 0.0851 | 32 | 0 | 5 | 8 | 5 | 50 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 507.5136 | 2 | YES | 0.77739 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 400 |  | 12 |  | 38 | 76 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 1421-PDB-4-0001 | PMCC-1 | OUTGOING FEEDER FOR PDB-1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 363.56 | kW | 3Ph | 400 | 0.85 | 0.951 | 649.1854 | 0 | 0.00 | 65 | 0 | 0 | AIR | 1C | 500 | 1C X 500 | 1C X 500 | 0.6/1.0 | 704 | 0.0774 | 0.0851 | 16 | 0 | 5 | 8 | 3 | 32 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 507.5136 | 2 | YES | 0.49753 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 2R x 0.6/1.0kV x 1C x 500 Sqmm/Phase | 256 |  | 12 |  | 38 | 76 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 5 | YES | 0.76256 | YES | NA | NA | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 555 |  | 30 |  | 42 | 630 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-1 (Neutral) | MAIN SUBSTATION BUILDING | A | POWER | 923.7875 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 1436.3645 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 0.73379 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 630 Sqmm | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 111 |  | 6 |  | 42 | 126 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 5 | YES | 0.76256 | YES | NA | NA | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 555 |  | 30 |  | 42 | 630 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 1421-ESWG-4-0001 | PMCC-1 | OUTGOING FEEDER FOR EPMCC - 1 / FEEDER-2 (Neutral) | MAIN SUBSTATION BUILDING | B | POWER | 923.7875 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 1436.3645 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 0.73379 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 630 Sqmm | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 111 |  | 6 |  | 42 | 126 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 1421-ESWG-4-0001 | EDG | EPMCC-1 (INCOMER-3 - DG) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 33 | 7 | 10 | 8 | 6 | 64 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 5 | YES | 1.319 | YES | NA | NA | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 5R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 960 |  | 30 |  | 42 | 630 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 1421-ESWG-4-0001 | EDG | EPMCC-1 (INCOMER-3 - DG Neutral) | MAIN SUBSTATION BUILDING |  | INCOMER | 923.7875 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 1436.3645 | 0 | 0.00 | 65 | 1 | 454.5455 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 33 | 7 | 10 | 8 | 6 | 64 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 1.2693 | YES | NA | NA | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 192 |  | 6 |  | 42 | 126 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | - | PMCC-1 | CRANE - Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) - Double Girder EOT Crane - (20T) | Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) | A | MOTOR | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 268.1272 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 29 | 275 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.8844 | YES | 6.88 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 385 |  | 2 | ACDEE1E2 | 33 | 33 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 0 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | - | PMCC-1 | CRANE - Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) - Double Girder EOT Crane - (20T)-Space Heater | Ammonia plant (Hydrogen Compressor: 1401- J202A, shed) | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 275 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.5813 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 385 |  | 2 | ACDEE1E2 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | - | PMCC-1 | CRANE- Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) - Double Girder EOT Crane - (20T) | Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) | B | MOTOR | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 268.1272 | 0.2 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 20 | 275 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.8169 | YES | 6.7192 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 376 |  | 2 | ACDEE1E2 | 33 | 33 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 0 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | - | PMCC-1 | CRANE- Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) - Double Girder EOT Crane - (20T)-Space Heater | Ammonia plant (Hydrogen Compressor: 1401- J203A, shed) | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 20 | 275 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 2.4732 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 376 |  | 2 | ACDEE1E2 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | - | PMCC-1 | Electric Hoist - Main substation building (Switchgear room) - Electric Hoist (2T) | Main Sub station building Switch gear Room | A | MOTOR | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 53.6254 | 0.2 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 0 | 5 | 8 | 5 | 47 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.92127 | YES | 1.3891 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 47 | Size changed to 25 to 4sqmm | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | - | PMCC-1 | Electric Hoist - Instrument air compressor building) - Electric Hoist (5T) | Instrument air compressor building) | B | MOTOR | 8 | kW | 3Ph | 400 | 0.85 | 0.95 | 14.3001 | 85.8007 | 0.2 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 20 | 168 | 38 | 8 | 24 | 258 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1599 | YES | 3.7187 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 258 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | - | PMCC-1 | CRANE- Air Separation unit - Single Girder EOT Crane - (8T) | Air Seperation unit | B | MOTOR | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 160.8763 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 142 | 38 | 8 | 22 | 239 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.7341 | YES | 4.9913 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 239 |  | 2 | ACDEE1E2 | 23 | 23 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 23 | 0 | 0 | 23 | 23 | 0 | 0 | 0 | 23 | 0 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 1421-SWG-4-0001 | PMCC-1 | PMCC-1(INCOMER 1) | MAIN SUBSTATION BUILDING |  | INCOMER | 3150 | kVA | 3Ph | 400 | 0.85043 | 0.91225 | 4984.1355 | LV BUSDUCT-400V | [110 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 1421-SWG-4-0001 | PMCC-1 | PMCC-1 (INCOMER 2) | MAIN SUBSTATION BUILDING |  | INCOMER | 3150 | kVA | 3Ph | 400 | 0.85043 | 0.91225 | 4984.1355 | LV BUSDUCT-400V | [110 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ASU PACKAGE DISTRIBUTION TRANSFORMER TO MCC PANEL | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 1421-ESWG-4-0001 | ASU package Transformer | ASU MCC Panel | AIR SEPARATION UNIT | B | POWER | 700 | kW | 3Ph | 400 | 0.84665 | 0.92832 | 1285.5453 | 0 | 0.00 | 50 | 1 | 349.6503 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 10 | 0 | 5 | 8 | 3 | 26 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 0.4615 | YES | NA | NA | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 234 |  | 18 |  | 42 | 378 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 1421-ESWG-4-0001 | ASU package Transformer | ASU MCC Panel Neutral | AIR SEPARATION UNIT | B | POWER | 404.157 | kW | 3Ph | 400 | 0.84665 | 0.92832 | 742.2317 | 0 | 0.00 | 50 | 1 | 349.6503 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 10 | 0 | 5 | 8 | 3 | 26 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 2 | YES | 0.39968 | YES | NA | NA | 2R x 0.6/1.0kV x 1C x 630 Sqmm | 2R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 52 |  | 4 |  | 42 | 84 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EPMCC-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 1400-P001A | EPMCC-1 | DIESEL OFFLOADING PUMP | Diesel storage area | A | MOTOR | 11 | kW | 3Ph | 400 | 0.75 | 0.853 | 24.8184 | 148.9107 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 152 | 10 | 8 | 21 | 229 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.9753 | YES | 5.7285 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 229 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 1400-P001B | EPMCC-1 | SPARE DIESEL OFFLOADING PUMP | Diesel storage area | B | MOTOR | 11 | kW | 3Ph | 400 | 0.75 | 0.853 | 24.8184 | 148.9107 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 30 | 162 | 10 | 8 | 21 | 230 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.9883 | YES | 5.7535 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 230 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 1401-PM124A | EPMCC-1 | COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.84 | 0.927 | 40.7808 | 244.6848 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 317 | 38 | 8 | 41 | 442 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.9989 | YES | 7.208 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 442 | initially 120sqmm with 322.5 mtr length ,now 95 sqm with 317 mtr | 2 | ACDEE1E2E3E4E5 | 33 | 33 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 |  | EPMCC-1 | SPACE HEATER COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 322.5 | 38 | 8 | 41 | 447.5 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.88305 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 447.5 |  | 2 | ACDEE1E2E3E4E5 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 1401-PM124B | EPMCC-1 | SPARE COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.84 | 0.927 | 40.7808 | 244.6848 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 322.5 | 38 | 8 | 40 | 438.5 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.9752 | YES | 7.151 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 438.5 |  | 2 | ACDEE1E2E3E4E5 | 33 | 33 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 |  | EPMCC-1 | SPACE HEATER SPARE COLD AMMONIA PRODUCT PUMP | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 322.5 | 38 | 8 | 40 | 438.5 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.86529 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 438.5 |  | 2 | ACDEE1E2E3E4E5 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 1401-PM104A | EPMCC-1 | BFW PUMP | AMMONIA PLANT | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.95 | 134.0636 | 804.3816 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 38 | 257 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 2.8699 | YES | 8.1539 | YES | 2R x 0.6/1kV x 3C x 150 Sqmm | 2R x 0.6/1kV x 3C x 150+PE Sqmm | 752 |  | 4 | ACDEE1E2E3 | 39 | 78 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 78 | 0 | 0 | 78 | 78 | 0 | 0 | 0 | 78 | 0 | 78 | 78 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 |  | EPMCC-1 | SPACE HEATER BFW PUMP | AMMONIA PLANT | A | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 257 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.74196 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 376 |  | 2 | ACDEE1E2E3 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 1401-PM104B | EPMCC-1 | SPARE BFW PUMP | AMMONIA PLANT | B | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.95 | 134.0636 | 804.3816 | 0.2 | 65 | 0 | 0 | AIR | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 258 | 38 | 8 | 34 | 368 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 2.8088 | YES | 7.9804 | YES | 2R x 0.6/1kV x 3C x 150 Sqmm | 2R x 0.6/1kV x 3C x 150+PE Sqmm | 736 |  | 4 | ACDEE1E2E3 | 39 | 78 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 78 | 0 | 0 | 78 | 78 | 0 | 0 | 0 | 78 | 0 | 78 | 78 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 |  | EPMCC-1 | SPACE HEATER SPARE BFW PUMP | AMMONIA PLANT | B | POWER | 0.06 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.32306 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 258 | 38 | 8 | 34 | 368 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.72617 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 368 |  | 2 | ACDEE1E2E3 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Ammonia Storage | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 1402-PK007 | EPMCC-1 | LP FLARE PACKAGE | AMMONIA STORAGE AREA | B | POWER | 0.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.89376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 424 | 38 | 8 | 50 | 549 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0761 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 549 |  | 2 | ACDEFGHIJ | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 |  | 1 |  |  |  | 1 | [44 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 16 | 0 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 1402-B001-TCP01 | EPMCC-1 | HEATER CONTROL PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481 |  | 2 | ACDEFGHIJ | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 |  | 1 |  |  |  | 1 | [44 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 16 | 0 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 1402-PK007 -CP01 | EPMCC-1 | IGNITION PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481 |  | 2 | ACDEFGHIJ | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 |  | 1 |  |  |  | 1 | [44 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 16 | 0 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 1402-PK007 -CP02 | EPMCC-1 | WINCH CONTROL PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481 |  | 2 | ACDEFGHIJ | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 |  | 1 |  |  |  | 1 | [44 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 16 | 0 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 1402-PK007 -CP03 | EPMCC-1 | AVIATION CONTROL PANEL (400V/230V) | AMMONIA STORAGE AREA | B | POWER | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 362 | 38 | 8 | 44 | 481 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8857 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 481 |  | 2 | ACDEFGHIJ | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 |  | 1 |  |  |  | 1 | [44 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 16 | 0 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 1402-PK006 | EPMCC-1 | HP FLARE PACKAGE | AMMONIA PLANT | A | POWER | 2.3 | kW | 1Ph | 230 | 0.85 | 0.95 | 12.3839 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 503 | 38 | 8 | 59 | 646 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.3325 | YES | NA | NA | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95 Sqmm | 646 |  | 2 | LMM1NO | 33 | 33 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | [27 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 33 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STEAM TURBINE GENERATOR | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 1401-P-1603 | EPMCC-1 | Emergency oil pump (110V) | AMMONIA PLANT | A | POWER | 2.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 11.8455 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 38 | 335 | 38 | 8 | 42 | 461 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 2.1448 | YES | NA | NA | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70 Sqmm | 461 |  | 2 | ACDEE1E2E3E4E5 | 30 | 30 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 30 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | - | EPMCC-1 | Monitoring cabinets (230V/110V) | AMMONIA PLANT | A | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 335 | 38 | 8 | 42 | 461 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.0713 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 461 |  | 2 | ACDEE1E2E3E4E5 | 26 | 26 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | 1 | [54 empty] | 0 | 26 | 0 | 0 | 26 | 26 | 0 | 0 | 0 | 26 | 0 | 26 | 26 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | ASU PACKAGE | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | ASU-EXPANDER OIL SUPPLY PUMP A | AIR SEPARATION UNIT | A | MOTOR | 5 | kW | 3Ph | 400 | 0.82 | 0.896 | 9.8229 | 58.9375 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 35 | 123 | 22 | 8 | 19 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | ASU-EXPANDER OIL SUPPLY PUMP B | AIR SEPARATION UNIT | B | MOTOR | 5 | kW | 3Ph | 400 | 0.82 | 0.896 | 9.8229 | 58.9375 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 123 | 22 | 8 | 19 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | ASU-CONTROL SYSTEM | AIR SEPARATION UNIT | A | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 35 | 163 | 22 | 8 | 23 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | Synthesis Gas compressor 1401-J-103 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 1401-PM103B | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J103 | AMMONIA PLANT | A | MOTOR | 37 | kW | 3Ph | 400 | 0.85 | 0.952 | 65.9991 | 395.9946 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 289 | 38 | 8 | 38 | 411 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 2 | YES | 2.2738 | YES | 5.4236 | YES | 2R x 0.6/1kV x 3C x 95 Sqmm | 2R x 0.6/1kV x 3C x 95+PE Sqmm | 822 |  | 4 | ACDEE1E2E3 | 33 | 66 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 66 | 0 | 0 | 66 | 66 | 0 | 0 | 0 | 66 | 0 | 66 | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | - | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J103-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 289 | 38 | 8 | 38 | 411 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 2 | YES | 1.3517 | YES | NA | NA | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 822 |  | 4 | ACDEE1E2E3 | 14 | 28 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 28 | 0 | 0 | 28 | 28 | 0 | 0 | 0 | 28 | 0 | 28 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 1401-PM103A | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J103 | AMMONIA PLANT | B | MOTOR | 37 | kW | 3Ph | 400 | 0.85 | 0.952 | 65.9991 | 395.9946 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 30 | 289 | 38 | 8 | 37 | 402 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 2.996 | YES | 6.4478 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 804 |  | 4 | ACDEE1E2E3 | 30 | 60 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 60 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 60 | 0 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J103-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 289 | 38 | 8 | 37 | 402 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 2 | YES | 1.3221 | YES | NA | NA | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 2R x 0.6/1kV x 3C x 2.5 Sqmm | 804 |  | 4 | ACDEE1E2E3 | 14 | 28 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | [56 empty] | 0 | 28 | 0 | 0 | 28 | 28 | 0 | 0 | 0 | 28 | 0 | 28 | 28 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J103 | AMMONIA PLANT | A | MOTOR | 2.2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.5783 | 27.4699 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 35 | 290 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 304 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 304 | 38 | 8 | 39 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J105 | AMMONIA PLANT | B | MOTOR | 2.2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.5783 | 27.4699 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 304 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J105 | AMMONIA PLANT | A | POWER | 17.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 31.2815 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 35 | 304 | 38 | 8 | 39 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | UCP FANS & LIGHTNING FOR 1401-J105 | AMMONIA PLANT | B | POWER | 3.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 6.2563 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 304 | 38 | 8 | 38 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | Synthesis Gas compressor 1401-J-105 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 1401-PM105A | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | A | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.9026 | YES | 7.0874 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 427 |  | 2 | ACDEE1E2E3E4 | 33 | 33 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 |  | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J105-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.7538 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 427 |  | 2 | ACDEE1E2E3E4 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 1401-PM105B | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J105 | AMMONIA PLANT | B | MOTOR | 22 | kW | 3Ph | 400 | 0.82 | 0.933 | 41.5068 | 249.0408 | 0.2 | 50 | 0 | 0 | AIR | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 304 | 38 | 8 | 38 | 418 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.8414 | YES | 6.938 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 418 |  | 2 | ACDEE1E2E3E4 | 33 | 33 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 33 | 0 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 |  | EPMCC-1 | SPARE LUBE OIL PUMP FOR 1401-J105-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 304 | 38 | 8 | 38 | 418 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.7169 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 418 |  | 2 | ACDEE1E2E3E4 | 15 | 15 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 0 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 1401-CM115 | EPMCC-1 | OIL DEMISTER FAN MOTOR FOR 1401-J105 | AMMONIA PLANT | A | MOTOR | 2.2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.5783 | 27.4699 | 0.2 | 50 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 38 | 304 | 38 | 8 | 39 | 427 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.714 | YES | 4.4512 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 427 |  | 2 | ACDEE1E2E3E4 | 16 | 16 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 16 | 0 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N2 Compressor | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | - | EPMCC-1 | AUXILIARY LUBE OIL PUMP FOR 1401-J201 | AMMONIA PLANT | A | MOTOR | 3.7 | kW | 3Ph | 400 | 0.82 | 0.896 | 7.269 | 43.6137 | 0.2 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 289 | 38 | 8 | 38 | 411 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.6487 | YES | 4.4076 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | 411 |  | 2 | ACDEE1E2E3E4 | 19 | 19 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | 1 | 1 | [55 empty] | 0 | 19 | 0 | 0 | 19 | 19 | 0 | 0 | 0 | 19 | 0 | 19 | 19 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | MIST ELIMINATOR MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 1.5 | kW | 3Ph | 400 | 0.75 | 0.853 | 3.3843 | 20.306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 270 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | A | MOTOR | 1.1 | kW | 3Ph | 400 | 0.8 | 0.841 | 2.3599 | 14.1596 | 0.2 | 50 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 35 | 270 | 38 | 8 | 36 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | NOISE ENCLOSURE FANS MOTOR FOR 1401-J201 | AMMONIA PLANT | B | MOTOR | 1.1 | kW | 3Ph | 400 | 0.8 | 0.841 | 2.3599 | 14.1596 | 0.2 | 50 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 270 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | A | POWER | 4.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.0438 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 35 | 270 | 38 | 8 | 36 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | LUBE OIL ELECTRIC HEATER A for 1401-J201 | AMMONIA PLANT | B | POWER | 4.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.0438 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 270 | 38 | 8 | 35 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | PLC PANEL (01 Qty),PLC PANEL UTILITIES (FANS,LIGHTS,SOCKETS-01Qty),LOCAL CONTROL PANEL (01 Qty) FOR 1401-J201 | AMMONIA PLANT | A | POWER | 2.2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.9325 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 35 | 270 | 38 | 8 | 36 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | Auxiliary H2 Compressor (1401-J-202A/B) | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J202A | AMMONIA PLANT | A | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
146 | 1401-P202C | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J202A | AMMONIA PLANT | B | MOTOR | 9.3 | kW | 3Ph | 400 | 0.84 | 0.927 | 17.2392 | 103.4349 | 0.2 | 50 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 30 | 237 | 38 | 8 | 32 | 345 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.5122 | YES | 4.6325 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 345 |  | 2 | ACDEE1E2 | 23 | 23 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 23 | 0 | 0 | 23 | 23 | 0 | 0 | 0 | 23 | 0 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J202A | AMMONIA PLANT | A | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J202A | AMMONIA PLANT | B | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
147 | 1401-BM202A | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J202A | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4137 | YES | 4.4356 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 388 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J202A | AMMONIA PLANT | A | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202A | AMMONIA PLANT | B | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J202A | AMMONIA PLANT | B | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 185 | 3.5C X 185 | 3.5C X 185 | 0.6/1.0 | 338 | 0.21 | 0.0727 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 185 Sqmm | 1R x 0.6/1kV x 3.5C x 185 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
148 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.8047 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | REMOTE I/O CABINET FOR 1401-J202A | AMMONIA PLANT | B | POWER | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MMS CABINET FOR1401-J202A | AMMONIA PLANT | A | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J202B | AMMONIA PLANT | B | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
149 | 1401-P202D | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J202B | AMMONIA PLANT | A | MOTOR | 9.3 | kW | 3Ph | 400 | 0.84 | 0.927 | 17.2392 | 103.4349 | 0.2 | 50 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 38 | 269 | 38 | 8 | 36 | 389 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.8326 | YES | 5.2233 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | 389 |  | 2 | ACDEE1E2 | 23 | 23 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 23 | 0 | 0 | 23 | 23 | 0 | 0 | 0 | 23 | 0 | 23 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J202B | AMMONIA PLANT | B | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J202B | AMMONIA PLANT | A | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
150 | 1401-BM202B | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J202B | AMMONIA PLANT | B | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 33 | 271 | 38 | 8 | 35 | 385 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.395 | YES | 4.4013 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 385 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J202B | AMMONIA PLANT | A | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J202B | AMMONIA PLANT | B | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J202B | AMMONIA PLANT | A | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 240 | 3.5C X 240 | 3.5C X 240 | 0.6/1.0 | 401 | 0.16 | 0.0719 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 240 Sqmm | 1R x 0.6/1kV x 3.5C x 240 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
151 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | B | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 80 | 5 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6927 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 136 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | REMOTE I/O CABINET FOR 1401-J202B | AMMONIA PLANT | A | POWER | 4 | kW | 3Ph | 400 | 0.85 | 0.95 | 7.1501 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MMS CABINET FOR 1401-J202B | AMMONIA PLANT | B | POWER | 2 | kW | 3Ph | 400 | 0.85 | 0.95 | 3.575 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
152 | 1401-PM202G | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 2 | YES | 2.4404 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 776 |  | 4 | ACDEE1E2 | 30 | 60 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 60 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 60 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 |  | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 |  | EPMCC-1 | ISC PANEL (NON-UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 |  | EPMCC-1 | ISC PANEL (REDUNDANT UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 1401-PM202H | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 22 | kW | 3Ph | 400 | 0.85 | 0.95 | 39.3253 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 268 | 38 | 8 | 36 | 388 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 2 | YES | 2.4404 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 776 |  | 4 | ACDEE1E2 | 30 | 60 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 60 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 60 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 |  | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J202A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 |  | EPMCC-1 | ISC PANEL (NON-UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 |  | EPMCC-1 | ISC PANEL (REDUNDANT UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Auxiliary H2 Compressor (1401-J-203B) | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 1401-P203C | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J203A | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.84 | 0.927 | 10.1952 | 61.1712 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 247 | 38 | 8 | 34 | 365 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1558 | YES | 3.7507 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 365 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | MAIN LUBE OIL PUMP FOR 1401-J203A | AMMONIA PLANT | B | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
161 | 1401-P203E | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B | AMMONIA PLANT | A | MOTOR | 30 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 38 | 247 | 38 | 8 | 34 | 365 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 2.201 | YES | 4.7369 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 730 |  | 4 | ACDEE1E2 | 30 | 60 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 60 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 60 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | - | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B-SPACE HEATER | AMMONIA PLANT | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 38 | 247 | 38 | 8 | 34 | 365 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 2.4008 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 365 |  | 2 | ACDEE1E2 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 1401-P203F | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B | AMMONIA PLANT | B | MOTOR | 30 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 30 | 247 | 38 | 8 | 33 | 356 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 2.1467 | YES | 4.6201 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 712 |  | 4 | ACDEE1E2 | 30 | 60 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 60 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 60 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | - | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J203A/B & 1401-J202A/B-SPACE HEATER | AMMONIA PLANT | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 30 | 247 | 38 | 8 | 33 | 356 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 2.3416 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 356 |  | 2 | ACDEE1E2 | 14 | 14 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 14 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 14 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 1401-BM203A | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J203A | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 257 | 38 | 8 | 35 | 376 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.339 | YES | 4.2984 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 376 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J203A | AMMONIA PLANT | B | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203A | AMMONIA PLANT | A | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 35 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J203A | AMMONIA PLANT | B | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 240 | 3.5C X 240 | 3.5C X 240 | 0.6/1.0 | 401 | 0.16 | 0.0719 | 29 | 237 | 38 | 8 | 32 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 240 Sqmm | 1R x 0.6/1kV x 3.5C x 240 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
166 | 1401-P203D | EPMCC-1 | AUX. LUBE OIL PUMP FOR 1401-J203B | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.84 | 0.927 | 10.1952 | 61.1712 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 248 | 38 | 8 | 34 | 366 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.1617 | YES | 3.761 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 366 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | LATER | EPMCC-1 | MAIN LUBE OIL PUMP FOR1401-J203B | AMMONIA PLANT | B | MOTOR | 15 | kW | 3Ph | 400 | 0.84 | 0.927 | 27.8051 | 166.8306 | 0.2 | 50 | 0 | 0 | AIR | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 70 Sqmm | 1R x 0.6/1kV x 3C x 70+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | LATER | EPMCC-1 | MAIN COOLENT PUMP FOR 1401-J203B | AMMONIA PLANT | A | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 120 | 3C X 120 | 3C X 120+PE | 0.6/1.0 | 257 | 0.324 | 0.0726 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 1R x 0.6/1kV x 3C x 120+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | LATER | EPMCC-1 | AUX. COOLENT PUMP FOR 1401-J203B | AMMONIA PLANT | B | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 50 | 0 | 0 | AIR | 3C | 240 | 3C X 240 | 3C X 240+PE | 0.6/1.0 | 401 | 0.16 | 0.0719 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | 0 | YES | 1R x 0.6/1kV x 3C x 240 Sqmm | 1R x 0.6/1kV x 3C x 240+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
167 | 1401-BM203B | EPMCC-1 | BARRING DEVICE MOTOTR FOR 1401-J203B | AMMONIA PLANT | A | MOTOR | 5.5 | kW | 3Ph | 400 | 0.79 | 0.886 | 11.3421 | 68.0527 | 0.2 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25+PE | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 263 | 38 | 8 | 35 | 382 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.3763 | YES | 4.367 | YES | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25+PE Sqmm | 382 |  | 2 | ACDEE1E2 | 21 | 21 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | FRAME OIL HEATER FOR 1401-J203 | AMMONIA PLANT | B | POWER | 25 | kW | 3Ph | 400 | 0.85 | 0.95 | 44.6879 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | MAIN MOTOR SPACE HEATER FOR 1401-J203 B | AMMONIA PLANT | A | POWER | 1.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 2.6813 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 35 | 255 | 38 | 8 | 34 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | EPMCC-1 | WATER TANK HEATER FOR 1401-J203B | AMMONIA PLANT | B | POWER | 40 | kW | 3Ph | 400 | 0.85 | 0.95 | 71.5006 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 240 | 3.5C X 240 | 3.5C X 240 | 0.6/1.0 | 401 | 0.16 | 0.0719 | 29 | 255 | 38 | 8 | 33 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 240 Sqmm | 1R x 0.6/1kV x 3.5C x 240 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
168 | 1401-P203A | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 11 | kW | 3Ph | 400 | 0.85 | 0.95 | 19.6627 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 263 | 38 | 8 | 35 | 382 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.4026 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 382 |  | 2 | ACDEE1E2 | 30 | 30 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 30 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 30 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J203A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.8047 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | - | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J203A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | - | EPMCC-1 | ISC PANEL (NON-UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | - | EPMCC-1 | ISC PANEL (REDUNDANT UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | - | EPMCC-1 | HPU system motor | AMMONIA PLANT | A | POWER | 11 | kW | 3Ph | 400 | 0.85 | 0.95 | 19.6627 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 38 | 263 | 38 | 8 | 35 | 382 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.4026 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 382 |  | 2 | ACDEE1E2 | 30 | 30 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | 1 | [57 empty] | 0 | 30 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 30 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | - | EPMCC-1 | UCP CABINET (NON-UPS) FOR 1401-J203B (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.45 | kW | 1Ph | 230 | 0.85 | 0.95 | 7.8072 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.8047 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | - | EPMCC-1 | UCP CABINET (REDUNDANT UPS) FOR 1401-J203A (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 1.8 | kW | 1Ph | 230 | 0.85 | 0.95 | 9.6917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2403 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 145 |  | 2 | AB | 19 | 19 |  | 1 | 1 | [67 empty] | 0 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | - | EPMCC-1 | ISC PANEL (NON-UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.18 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.96917 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.53601 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | - | EPMCC-1 | ISC PANEL (REDUNDANT UPS) (230 V) | CENTRAL CONTROL BUILDING | A | POWER | 0.81 | kW | 1Ph | 230 | 0.85 | 0.95 | 4.3613 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 80 | 5 | 8 | 14 | 145 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.412 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 145 |  | 2 | AB | 15 | 15 |  | 1 | 1 | [67 empty] | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sea water intake outfall package _ Intake facilities/Intake Structure package (connected load) | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | EPMCC-1 | MOV ON Screen Backwash pump | SEA WATER INTAKE FACILITY | A | MOTOR | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 10.7251 | 0.2 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16+PE | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 1242 | 38 | 8 | 133 | 1459 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3906 | YES | 3.8476 | YES | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16+PE Sqmm | [7 empty] | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 |  | 1 |  |  |  |  | 1 | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Cooling Tower package | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | - | EPMCC-1 | MOV ON COOLING WATER BYPASS LINE | COOLING TOWER AREA | B | MOTOR | 1 | kW | 3Ph | 400 | 0.85 | 0.95 | 1.7875 | 10.7251 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 190 | 38 | 8 | 28 | 302 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.1839 | YES | 1.7851 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 302 |  | 2 | AQQ2RR1R1.A | 15 | 15 |  | 1 | [43 empty] | 1 |  | 1 | [6 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 1421-UPS-5-0001 | EPMCC-1 | OUTGOING FEEDER FOR UPS -1 / MAIN SUBSTATION - FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 212.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 379.8468 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 38 | 20 | 6 | 8 | 8 | 80 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 3 | YES | 1.1534 | YES | NA | NA | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 240 |  | 6 | A1 | 48 | 144 | 1 | [69 empty] | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 1421-UPS-5-0001 | EPMCC-1 | OUTGOING FEEDER FOR UPS -1 / MAIN SUBSTATION - FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 212.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 379.8468 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 20 | 6 | 8 | 7 | 71 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 3 | YES | 1.0236 | YES | NA | NA | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 213 |  | 6 | A1 | 48 | 144 | 1 | [69 empty] | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 1421-UPS-5-0001 | EPMCC-1 | OUTGOING FEEDER FOR UPS -1 / MAIN SUBSTATION - FEEDER-3 | MAIN SUBSTATION BUILDING | B | POWER | 212.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 379.8468 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 20 | 6 | 8 | 7 | 71 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 3 | YES | 1.0236 | YES | NA | NA | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 3R x 0.6/1kV x 3.5C x 150 Sqmm | 213 |  | 6 | A1 | 48 | 144 | 1 | [69 empty] | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 1421-BC-6-0001 | EPMCC-1 | OUTGOING FEEDER FOR BATTERY CHARGER - MAIN SUBSTATION - FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 100 | kW | 3Ph | 400 | 0.85 | 0.95 | 178.7515 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.58008 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 114 |  | 4 |  | 48 | 96 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 1421-BC-6-0002 | EPMCC-1 | OUTGOING FEEDER FOR BATTERY CHARGER - MAIN SUBSTATION - FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 100 | kW | 3Ph | 400 | 0.85 | 0.95 | 178.7515 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 30 | 0 | 5 | 8 | 5 | 48 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.48849 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 96 |  | 4 |  | 48 | 96 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 1421-EMLDB-4-0001 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-1 (MAIN SUBSTATION BUILDING) | MAIN SUBSTATION BUILDING | A | POWER | 21.25 | kW | 3Ph | 400 | 0.85 | 0.95 | 37.9847 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.2675 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 57 |  | 2 |  | 25 | 25 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 1420-EMLDB-4-0002 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-2 (COOLING TOWER SUBSTATION) | COOLING TOWER SUBSTATION | B | POWER | 29.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 53.1786 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 30 | 88 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.8015 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 150 |  | 2 | AQQ1 | 36 | 36 |  | 1 | [43 empty] | 1 | 1 | [23 empty] | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 1402-EMLDB-4-0003 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-3 (NH3 STORAGE SUBSTATION) | AMMONIA STORAGE SUBSTATION | B | POWER | 12.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 22.7908 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 365 | 38 | 8 | 45 | 486 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.8569 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 486 |  | 2 | ACDEFGIJ | 39 | 39 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 39 | 0 | 0 | 39 | 39 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 1409-EMLDB-4-0004 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-4 (SEA WATER TREATMENT SUBSTATION) | SEA WATER TREATMENT SUBSTATION | A | POWER | 12.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 22.7908 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 38 | 340 | 38 | 8 | 43 | 467 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 2.4037 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 467 |  | 2 | ACDEFGHH1 | 36 | 36 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 | 1 | [49 empty] | 0 | 36 | 0 | 0 | 36 | 36 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 1409-EMLDB-4-0005 | EPMCC-1 | OUTGOING FEEDER FOR EMERGENCY MAIN LIGHTING DB-5 (ELECTROLYZER SUBSTATION) | ELECTROLYZER SUBSTATION | A | POWER | 20 | kW | 3Ph | 400 | 0.85 | 0.95 | 35.7503 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 35 | 144 | 20 | 8 | 21 | 228 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.8409 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 228 |  | 2 | LL1L2L3 | 36 | 36 | [27 empty] | 1 | 1 | 1 | 1 | [39 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 1421-ESWG-4-0001 | PMCC-1 | EPMCC-1 (INCOMER-1) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 1421-ESWG-4-0001 | PMCC-1 | EPMCC-1 (INCOMER-2) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 1421-ESWG-4-0001 | EDG | EPMCC-1 (INCOMER-3 - DG) | MAIN SUBSTATION BUILDING |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84665 | 0.92832 | 2487.7833 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | PDB-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | HVAC SYSTEM | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | - | PDB-1 | ROOFTOP UNIT-1 | CENTRAL CONTROL BUILDING | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.954 | 133.5015 | 801.0089 | 0.2 | 50 | 0 | 0 | TRENCH | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 1.5528 | YES | 3.3418 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 206 |  | 4 | ABB1 | 30 | 60 |  | 1 | 1 | 1 | [66 empty] | 0 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | - | PDB-1 | ROOFTOP UNIT-1-SPACE HEATER | CENTRAL CONTROL BUILDING | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.6775 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 103 |  | 2 | ABB1 | 14 | 14 |  | 1 | 1 | 1 | [66 empty] | 0 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | - | PDB-1 | HEATER-1 | CENTRAL CONTROL BUILDING | A | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6168 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103 |  | 2 | ABB1 | 25 | 25 |  | 1 | 1 | 1 | [66 empty] | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | - | PDB-1 | HUMIDIFIER-1 | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9401 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103 |  | 2 | ABB1 | 25 | 25 |  | 1 | 1 | 1 | [66 empty] | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | - | PDB-1 | ROOFTOP UNIT-2 | CENTRAL CONTROL BUILDING | B | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.954 | 133.5015 | 801.0089 | 0.2 | 50 | 0 | 0 | TRENCH | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 1.5528 | YES | 3.3418 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 206 |  | 4 | ABB1 | 30 | 60 |  | 1 | 1 | 1 | [66 empty] | 0 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | - | PDB-1 | ROOFTOP UNIT-2-SPACE HEATER | CENTRAL CONTROL BUILDING | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.6775 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 103 |  | 2 | ABB1 | 14 | 14 |  | 1 | 1 | 1 | [66 empty] | 0 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | - | PDB-1 | HEATER-2 | CENTRAL CONTROL BUILDING | B | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6168 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103 |  | 2 | ABB1 | 25 | 25 |  | 1 | 1 | 1 | [66 empty] | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | - | PDB-1 | HUMIDIFIER-2 | CENTRAL CONTROL BUILDING | B | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9401 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103 |  | 2 | ABB1 | 25 | 25 |  | 1 | 1 | 1 | [66 empty] | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | - | PDB-1 | ROOFTOP UNIT-3 | CENTRAL CONTROL BUILDING | A | MOTOR | 75 | kW | 3Ph | 400 | 0.85 | 0.954 | 133.5015 | 801.0089 | 0.2 | 50 | 0 | 0 | TRENCH | 3C | 70 | 3C X 70 | 3C X 70+PE | 0.6/1.0 | 177 | 0.567 | 0.0752 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 1.5528 | YES | 3.3418 | YES | 2R x 0.6/1kV x 3C x 70 Sqmm | 2R x 0.6/1kV x 3C x 70+PE Sqmm | 206 |  | 4 | ABB1 | 30 | 60 |  | 1 | 1 | 1 | [66 empty] | 0 | 60 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | - | PDB-1 | ROOFTOP UNIT-3-SPACE HEATER | CENTRAL CONTROL BUILDING | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.6775 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 103 |  | 2 | ABB1 | 14 | 14 |  | 1 | 1 | 1 | [66 empty] | 0 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | - | PDB-1 | HEATER-3 | CENTRAL CONTROL BUILDING | A | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6168 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103 |  | 2 | ABB1 | 25 | 25 |  | 1 | 1 | 1 | [66 empty] | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | - | PDB-1 | HUMIDIFIER-3 | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9401 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 103 |  | 2 | ABB1 | 25 | 25 |  | 1 | 1 | 1 | [66 empty] | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 1422-ACDB-4-0002 | PDB-1 | HVAC DB-001 | CENTRAL CONTROL BUILDING | B | POWER | 72.623 | kW | 3Ph | 400 | 0.85 | 0.95 | 129.8147 | 0 | 0.00 | 50 | 0 | 0 | TRENCH | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.2416 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 103 |  | 2 | ABB1 | 39 | 39 |  | 1 | 1 | 1 | [66 empty] | 0 | 39 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | - | PDB-1 | ROOFTOP UNIT1 | MAIN SUBSTATION BUILDING | B | MOTOR | 62 | kW | 3Ph | 400 | 0.85 | 0.954 | 110.3612 | 662.1673 | 0.2 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 2 | YES | 1.2179 | YES | 2.3899 | YES | 2R x 0.6/1kV x 3C x 50 Sqmm | 2R x 0.6/1kV x 3C x 50+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | - | PDB-1 | ROOFTOP UNIT1-SPACE HEATER | MAIN SUBSTATION BUILDING | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.45386 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | - | PDB-1 | HEATER-1 | MAIN SUBSTATION BUILDING | B | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6959 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | - | PDB-1 | HUMIDIFIER-1 | MAIN SUBSTATION BUILDING | B | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | - | PDB-1 | ROOFTOP UNIT2 | MAIN SUBSTATION BUILDING | A | MOTOR | 45 | kW | 3Ph | 400 | 0.85 | 0.954 | 80.1009 | 480.6053 | 0.2 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.7679 | YES | 3.4692 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | - | PDB-1 | ROOFTOP UNIT2-SPACE HEATER | MAIN SUBSTATION BUILDING | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.45386 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | - | PDB-1 | HEATER-2 | MAIN SUBSTATION BUILDING | A | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6959 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | - | PDB-1 | HUMIDIFIER-2 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | - | PDB-1 | VFD ROOM - SPLIT AC 1 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | - | PDB-1 | VFD ROOM - SPLIT AC 2 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | - | PDB-1 | VFD ROOM - SPLIT AC 3 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | - | PDB-1 | VFD ROOM - SPLIT AC 4 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | - | PDB-1 | VFD ROOM - SPLIT AC 5 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | - | PDB-1 | VFD ROOM - SPLIT AC 6 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | - | PDB-1 | VFD ROOM - SPLIT AC 7 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | - | PDB-1 | VFD ROOM - SPLIT AC 8 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | - | PDB-1 | VFD ROOM - SPLIT AC 9 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | - | PDB-1 | VFD ROOM - SPLIT AC 10 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | - | PDB-1 | VFD ROOM - SPLIT AC 11 | MAIN SUBSTATION BUILDING | B | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.0798 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 103 |  | 2 | ABB1 | 26 | 26 |  | 1 | 1 | 1 | [66 empty] | 0 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | - | PDB-1 | BATTERY ROOM-VENTILATION FAN 1 | MAIN SUBSTATION BUILDING | A | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.98313 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.14878 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 69 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | - | PDB-1 | BATTERY ROOM-VENTILATION FAN 2 | MAIN SUBSTATION BUILDING | A | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.98313 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.14878 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 69 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | - | PDB-1 | LV SWITCHGEAR ROOM VENTILATION FAN 1 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 69 |  | 2 |  | 18 | 18 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | - | PDB-1 | LV SWITCHGEAR ROOM VENTILATION FAN 2 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 69 |  | 2 |  | 18 | 18 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | - | PDB-1 | LV SWITCHGEAR ROOM VENTILATION FAN 3 | MAIN SUBSTATION BUILDING | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.814 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 69 |  | 2 |  | 18 | 18 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | - | PDB-1 | MV SWITCHGEAR ROOM VENTILATION FAN 1 | MAIN SUBSTATION BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 2 | YES | 1.6326 | YES | NA | NA | 2R x 0.6/1kV x 4C x 6 Sqmm | 2R x 0.6/1kV x 4C x 6 Sqmm | 138 |  | 4 |  | 18 | 36 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | - | PDB-1 | MV SWITCHGEAR ROOM VENTILATION FAN 2 | MAIN SUBSTATION BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 2 | YES | 1.6326 | YES | NA | NA | 2R x 0.6/1kV x 4C x 6 Sqmm | 2R x 0.6/1kV x 4C x 6 Sqmm | 138 |  | 4 |  | 18 | 36 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | - | PDB-1 | MV SWITCHGEAR ROOM VENTILATION FAN 3 | MAIN SUBSTATION BUILDING | A | POWER | 18 | kW | 3Ph | 400 | 0.85 | 0.95 | 32.1753 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 2 | YES | 1.6326 | YES | NA | NA | 2R x 0.6/1kV x 4C x 6 Sqmm | 2R x 0.6/1kV x 4C x 6 Sqmm | 138 |  | 4 |  | 18 | 36 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | - | PDB-1 | ELECTRICAL SHIFT INCHARGE RM - SPLIT AC 1 | MAIN SUBSTATION BUILDING | A | POWER | 4 | kW | 1Ph | 230 | 0.85 | 0.95 | 21.5372 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3691 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | - | PDB-1 | BATTERY ROOM - SPLIT AC 1 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | - | PDB-1 | BATTERY ROOM - SPLIT AC 2 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | - | PDB-1 | BATTERY ROOM - SPLIT AC 3 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | - | PDB-1 | BATTERY ROOM - SPLIT AC 4 | MAIN SUBSTATION BUILDING | A | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 10 | 10 | 8 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0729 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVAC - EMERGENCY LOADS
CONTROL BUILDING
222 | - | PDB-1 | GROUND FLOOR - EXHAUST FAN | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | - | PDB-1 | GROUND FLOOR - FRESH AIR FAN | CENTRAL CONTROL BUILDING | A | POWER | 18 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | - | PDB-1 | UPS ROOM - EXHAUST FAN | CENTRAL CONTROL BUILDING | A | POWER | 1.1 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | - | PDB-1 | BATTERY ROOM - EXHAUST FAN | CENTRAL CONTROL BUILDING | A | POWER | 1.1 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 34 | 41 | 10 | 8 | 10 | 103 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.9762 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 103 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other Load | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 1421-ACDB-4-0001 | PDB-1 | OUTGOING FEEDER FOR 400V ACDB-1 / FEEDER-1 | MAIN SUBSTATION BUILDING | A | POWER | 31.0737 | kW | 3Ph | 400 | 0.85 | 0.95 | 55.5447 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.008 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 31 |  | 2 |  | 25 | 25 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | 1421-ACDB-4-0001 | PDB-1 | OUTGOING FEEDER FOR 400V ACDB-1 / FEEDER-2 | MAIN SUBSTATION BUILDING | B | POWER | 31.0737 | kW | 3Ph | 400 | 0.85 | 0.95 | 55.5447 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.008 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 31 |  | 2 |  | 25 | 25 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 1421-PDB-4-0001 | PMCC-1 | PDB - 1 (INCOMER 1) | MAIN SUBSTATION BUILDING |  | INCOMER | 343.1937 | kW | 3Ph | 400 | 0.85 | 0.951 | 612.8186 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 1421-PDB-4-0001 | PMCC-1 | PDB - 1 (INCOMER 2) | MAIN SUBSTATION BUILDING |  | INCOMER | 343.1937 | kW | 3Ph | 400 | 0.85 | 0.951 | 612.8186 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ACDB-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 1421-SWG-1-0001 | ACDB-1 | AUX POWER SUPPLY - 33kV SWITCHGEAR - 1 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 36 | 0 | 5 | 8 | 5 | 54 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0574 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 54 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 1421-SWG-1-0001 | ACDB-1 | AUX POWER SUPPLY - 33kV SWITCHGEAR - 2 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 36 | 0 | 5 | 8 | 5 | 54 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0574 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 54 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY - 11kV SWITCHGEAR - 1 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 25 | 0 | 5 | 8 | 4 | 42 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.8224 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 42 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY - 11kV SWITCHGEAR - 2 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 5 | 8 | 5 | 48 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.93988 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 48 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY - PMCC-1 (BUS-A) | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.60701 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 31 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY - PMCC-1 (BUS-B) | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.60701 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 31 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 1421-TFP-1-0001 | ACDB-1 | AUX POWER SUPPLY - POWER TRANSFORMER - 1 | MAIN SUBSTATION BUILDING |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 5 | 8 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.9581 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 50 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 1421-TFP-1-0002 | ACDB-1 | AUX POWER SUPPLY - POWER TRANSFORMER - 2 | MAIN SUBSTATION BUILDING |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 39 | 0 | 5 | 8 | 6 | 58 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 2.2714 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 58 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY SEGREGATED PHASE BUSDUCT SYSTEM-1A | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 34 | 0 | 5 | 8 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.0182 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 1421-SWG-2-0001 | ACDB-1 | AUX POWER SUPPLY SEGREGATED PHASE BUSDUCT SYSTEM-1B | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 41 | 0 | 5 | 8 | 6 | 60 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.1749 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 60 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY NSPBD SYSTEM-1A | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 9 | 0 | 5 | 8 | 3 | 25 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.48952 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 25 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 1421-SWG-4-0001 | ACDB-1 | AUX POWER SUPPLY NSPBD SYSTEM-1B | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 5 | 8 | 3 | 31 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.60701 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 31 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 1421-TFD-2-0001 | ACDB-1 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-1 | MAIN SUBSTATION BUILDING |  | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.3569 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 28 | 0 | 5 | 8 | 5 | 46 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.54043 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 46 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 1421-TFD-2-0002 | ACDB-1 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-2 | MAIN SUBSTATION BUILDING |  | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.3569 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 21 | 0 | 5 | 8 | 4 | 38 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.44644 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 38 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 1421-TFP-1-0001 | ACDB-1 | POWER TRANSFORMER OLTC-1 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 43 | 0 | 5 | 8 | 6 | 62 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.214 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 62 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 1421-TFP-1-0002 | ACDB-1 | POWER TRANSFORMER OLTC-2 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 50 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 43 | 0 | 5 | 8 | 6 | 62 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.214 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 62 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 1421-ACDB-4-0001 | PDB-1 | ACDB-1 (INCOMER 1) | MAIN SUBSTATION BUILDING |  | INCOMER | 28.2316 | kW | 3Ph | 400 | 0.85 | 0.951 | 50.4113 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 1421-ACDB-4-0001 | PDB-1 | ACDB-1 (INCOMER 2) | MAIN SUBSTATION BUILDING |  | INCOMER | 28.2316 | kW | 3Ph | 400 | 0.85 | 0.951 | 50.4113 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MLDB-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | NLP-001 | MLDB-01 | LIGHTING DB-001 | MAIN SUBSTATION BUILDING |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 27 | 0 | 5 | 5 | 4 | 41 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.31236 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 41 |  | 2 |  | 27 | 27 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | NLP-002 | MLDB-01 | LIGHTING DB-002 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 27 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.26284 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 69 |  | 2 | A1 | 27 | 27 | 1 | [69 empty] | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | NLP-003 | MLDB-01 | LIGHTING DB-003 | ASU PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 25 | 95 | 22 | 10 | 16 | 168 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.63996 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 168 |  | 2 | ACDD1 | 27 | 27 |  | 1 |  |  | 1 | 1 | 1 | [63 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | NLP-004 | MLDB-01 | LIGHTING DB-004 | AMMONIA PLANT |  | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.951 | 26.7845 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 25 | 205 | 38 | 10 | 28 | 306 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.851 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 306 |  | 2 | ACDEE1 | 36 | 36 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 36 | 0 | 0 | 36 | 36 | 0 | 0 | 0 | 36 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | NLP-005 | MLDB-01 | LIGHTING DB-005 | INSTRUMENT AIR PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 25 | 176 | 15 | 5 | 23 | 244 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.92947 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 244 |  | 2 | D3LMM1 | 27 | 27 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | NLP-006 | MLDB-01 | LIGHTING DB-006 | HYDROGEN STORAGE AREA |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 25 | 370 | 43 | 5 | 45 | 488 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.968 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 488 |  | 2 | LMM1NOO1 | 36 | 36 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 0 | 0 | 36 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | NLP-007 | MLDB-01 | STREET LIGHTING DB- 01 | MAIN SUBSTATION BUILDING |  | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.951 | 26.7845 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 29 | 0 | 10 | 5 | 5 | 49 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.55996 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 49 |  | 2 |  | 27 | 27 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | HM-001 | MLDB-01 | HIGH MAST-001 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 405 | 10 | 5 | 47 | 515 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.2555 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 515 |  | 2 | LMM1NOO1 | 27 | 27 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | HM-002 | MLDB-01 | HIGH MAST-002 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 525 | 10 | 5 | 59 | 647 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.5773 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 647 |  | 2 | LMM1NOO1 | 27 | 27 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | HM-003 | MLDB-01 | HIGH MAST-003 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 405 | 10 | 5 | 47 | 515 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.2555 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 515 |  | 2 | LMM1NOO1 | 27 | 27 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | HM-004 | MLDB-01 | HIGH MAST-004 | NEAR HYDROGEN STORAGE AREA |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 525 | 10 | 5 | 59 | 647 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.5773 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 647 |  | 2 | LMM1NOO1 | 27 | 27 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | HM-005 | MLDB-01 | HIGH MAST-005 | NEAR MAIN SUBSTATION AREA FIRE DRILL POINT |  | POWER | 3.2 | kW | 3Ph | 400 | 0.85 | 0.951 | 5.714 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 48 | 50 | 10 | 5 | 12 | 125 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.30474 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 125 |  | 2 | L | 27 | 27 | [27 empty] | 1 | [42 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 1421-MLDB-4-0001 | PMCC-1 | MAIN LIGHTING DB-001 (INCOMER-1) | MAIN SUBSTATION BUILDING |  | INCOMER | 127.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 320 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 1421-MLDB-4-0001 | PMCC-1 | MAIN LIGHTING DB-001 (INCOMER-2) | MAIN SUBSTATION BUILDING |  | INCOMER | 127.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 320 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EMLDB-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | ELP-001 | EMLDB-1 | EMERGENCY LIGHTING DB-001 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 12 | 0 | 5 | 5 | 3 | 25 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0.32802 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 25 |  | 2 |  | 20 | 20 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | ELP-002 | EMLDB-1 | EMERGENCY LIGHTING DB-002 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 30 | 26 | 10 | 5 | 8 | 79 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.0365 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 79 |  | 2 | A1 | 20 | 20 | 1 | [69 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | ELP-003 | EMLDB-01 | EMERGENCY LIGHTING DB-003 | ASU PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 36 | 96 | 22 | 10 | 17 | 181 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 2.3749 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 181 |  | 2 | ACDD1 | 20 | 20 |  | 1 |  |  | 1 | 1 | 1 | [63 empty] | 0 | 20 | 0 | 0 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | ELP-004 | EMLDB-01 | EMERGENCY LIGHTING DB-004 | AMMONIA PLANT |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 36 | 206 | 38 | 10 | 29 | 319 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.4303 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 319 |  | 2 | ACDEE1 | 27 | 27 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | ELP-005 | EMLDB-01 | EMERGENCY LIGHTING DB-005 | INSTRUMENT AIR PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 36 | 177 | 15 | 5 | 24 | 257 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1033 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 257 |  | 2 | D3LMM1 | 21 | 21 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | ELP-006 | EMLDB-01 | EMERGENCY LIGHTING DB-006 | HYDROGEN STORAGE AREA |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 |  | 371 | 43 | 5 | 42 | 461 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.4096 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 461 |  | 2 | LMM1NOO1 | 25 | 25 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | ELP-007 | EMLDB-01 | EMERGENCY STREET LIGHTING DB- 01 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 29 | 0 | 10 | 5 | 5 | 49 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0.64292 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 49 |  | 2 |  | 20 | 20 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 1421-EMLDB-4-0001 | EMLDB-1 | EMERGENCY MAIN LIGHTING DB-001 (INCOMER) | MAIN SUBSTATION BUILDING |  | INCOMER | 30 | kW | 3Ph | 400 | 0.85 | 0.951 | 63 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WDB-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | WSDB-001 | WDB-01 | POWER RECEPTACLE DB-001 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 13 | 0 | 5 | 5 | 3 | 26 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.099041 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 26 |  | 2 |  | 27 | 27 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | WSDB-002 | WDB-01 | POWER RECEPTACLE DB-002 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 28 | 25 | 10 | 5 | 7 | 75 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.2857 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 75 |  | 2 | A1 | 27 | 27 | 1 | [69 empty] | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | WSDB-003 | WDB-01 | POWER RECEPTACLE DB-003 | ASU PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 35 | 97 | 22 | 10 | 17 | 181 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.68948 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 181 |  | 2 | ACDD1 | 27 | 27 |  | 1 |  |  | 1 | 1 | 1 | [63 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | WSDB-004 | WDB-01 | POWER RECEPTACLE DB-004 | AMMONIA PLANT |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 35 | 207 | 38 | 10 | 29 | 319 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.2152 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 319 |  | 2 | ACDEE1 | 27 | 27 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | WSDB-005 | WDB-01 | POWER RECEPTACLE DB-005 | INSTRUMENT AIR PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 35 | 178 | 15 | 5 | 24 | 257 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.97899 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 257 |  | 2 | D3LMM1 | 27 | 27 | [8 empty] | 1 | [18 empty] | 1 | [9 empty] | 1 | 1 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | WSDB-006 | WDB-01 | POWER RECEPTACLE DB-006 | HYDROGEN STORAGE AREA |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 20 | 371 | 43 | 5 | 44 | 483 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.8399 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 483 |  | 2 | LMM1NOO1 | 27 | 27 | [27 empty] | 1 | [9 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | WS-001 & 002 | WDB-01 | WELDING SOCKET -001 & 002 | MAIN SUBSTATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 15 | 0 | 5 | 5 | 3 | 28 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.22915 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 28 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | WS-003 | WDB-01 | WELDING SOCKET -003 | CENTRAL CONTROL BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 28 | 30 | 10 | 5 | 8 | 81 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.66291 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 81 |  | 2 | A1 | 21 | 21 | 1 | [69 empty] | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | WS-004 & 005 | WDB-01 | WELDING SOCKET -004 & 005 | ASU/ INSTRUMENT AIR PACKAGE |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 36 | 97 | 22 | 8 | 17 | 180 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.4731 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 180 |  | 2 | ACDD1D2 | 21 | 21 |  | 1 |  |  | 1 | 1 | 1 | 1 | [62 empty] | 0 | 21 | 0 | 0 | 21 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | WS-006 & 007 | WDB-01 | WELDING SOCKET -006 & 007 | AMMONIA PLANT |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 36 | 207 | 38 | 8 | 29 | 318 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6621 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 318 |  | 2 | ACDEE1 | 25 | 25 |  | 1 |  |  | 1 | 1 |  |  |  | 1 |  | 1 | [58 empty] | 0 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 1421-WDB-4-0001 | PMCC-1 | WELDING & RECEPTACLE DB-001 (INCOMER) | MAIN SUBSTATION BUILDING |  | INCOMER | 42.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 320 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MAIN UPS DB-1 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 1422-UPS-SDB-4-0001 | MAIN UPS DB-1 | AC UPS SUB DB-1_FEEDER-1 | CENTRAL CONTROL BUILDING |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 320 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 12 | 14 | 5 | 8 | 4 | 43 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.78339 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 86 |  | 4 | A1 | 48 | 96 | 1 | [69 empty] | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 1422-UPS-SDB-4-0001 | MAIN UPS DB-1 | AC UPS SUB DB-1_FEEDER-2 | CENTRAL CONTROL BUILDING |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 320 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 12 | 14 | 5 | 8 | 4 | 43 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 2 | YES | 0.78339 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 2R x 0.6/1kV x 3.5C x 150 Sqmm | 86 |  | 4 | A1 | 48 | 96 | 1 | [69 empty] | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 1417-UPS-SDB-4-0002 | MAIN UPS DB-1 | AC UPS SUB DB-2_FEEDER | Electrolyzer Electrical Building |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 20 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 55 | 101 | 20 | 8 | 19 | 203 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.3768 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 203 |  | 2 | LL1L2 | 25 | 25 | [27 empty] | 1 | 1 | 1 | [40 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 1417-UPS-SDB-4-0003 | MAIN UPS DB-1 | AC UPS SUB DB-3_FEEDER | Electrolyzer Electrical Building |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 20 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 55 | 101 | 20 | 8 | 19 | 203 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.3768 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 203 |  | 2 | LL1L2 | 25 | 25 | [27 empty] | 1 | 1 | 1 | [40 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | 1402-UPS-SDB-4-0004 | MAIN UPS DB-1 | AC UPS SUB DB-4_FEEDER-1 | Ammonia Storage Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 16 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 7 | 373 | 20 | 8 | 41 | 449 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.298 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 449 |  | 2 | ACDEFGIJ | 30 | 30 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 30 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 1402-UPS-SDB-4-0004 | MAIN UPS DB-1 | AC UPS SUB DB-4_FEEDER-2 | Ammonia Storage Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 16 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 7 | 373 | 20 | 8 | 41 | 449 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.298 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 449 |  | 2 | ACDEFGIJ | 30 | 30 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 |  |  | 1 |  |  |  | 1 | [44 empty] | 0 | 30 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 1409-UPS-SDB-4-0005 | MAIN UPS DB-1 | AC UPS SUB DB-5_FEEDER-1 | Sea Water Treatment Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 32 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 332 | 20 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.3015 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 429 |  | 2 | ACDEFGHH1 | 39 | 39 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 | 1 | [49 empty] | 0 | 39 | 0 | 0 | 39 | 39 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 1409-UPS-SDB-4-0005 | MAIN UPS DB-1 | AC UPS SUB DB-5_FEEDER-2 | Sea Water Treatment Substation |  | POWER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 32 | 0 | 0.00 | 50 | 0 | 0 | AIR | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 30 | 332 | 20 | 8 | 39 | 429 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.3015 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 429 |  | 2 | ACDEFGHH1 | 39 | 39 |  | 1 |  |  | 1 | 1 |  |  |  | 1 | [7 empty] | 1 | 1 | 1 | 1 | [49 empty] | 0 | 39 | 0 | 0 | 39 | 39 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 1422-UPSDB-4-0001 | UPS-1 | AC UPSDB-1 (INCOMER-1) | CENTRAL CONTROL BUILDING |  | INCOMER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 400 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 1422-UPSDB-4-0001 | UPS-1 | AC UPSDB-1 (INCOMER-2) | CENTRAL CONTROL BUILDING |  | INCOMER |  | kW | 3Ph | 400 | 0.85 | 0.951 | 400 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CENTRAL CONTROL BUILDING HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - VENTILATION FAN 1 | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM 2 - VENTILATION FAN 2 | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 |  | CENTRAL CONTROL BUILDING HVAC DB | LADIES & GENTS TOILET - VENTILATION FAN | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 |  | CENTRAL CONTROL BUILDING HVAC DB | CLEAN AGENT ROOM | CENTRAL CONTROL BUILDING |  | POWER | 0.55 | kW | 3Ph | 400 | 0.85 | 0.951 | 0.9821 | 0 | 0.00 | 25 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.12708 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 59 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 1 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 3 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 |  | CENTRAL CONTROL BUILDING HVAC DB | UPS ROOM - SPLIT AC 4 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 |  | CENTRAL CONTROL BUILDING HVAC DB | INSTRUMENTATION MANAGER - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 |  | CENTRAL CONTROL BUILDING HVAC DB | APC/MES MANAGER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 |  | CENTRAL CONTROL BUILDING HVAC DB | GENTS PRAYER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 8.068 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8156 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 59 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 |  | CENTRAL CONTROL BUILDING HVAC DB | LADIES PRAYER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 |  | CENTRAL CONTROL BUILDING HVAC DB | SHIFT INCHARGE ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 8.068 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8156 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 59 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 |  | CENTRAL CONTROL BUILDING HVAC DB | NH3 PLANT MANAGER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 |  | CENTRAL CONTROL BUILDING HVAC DB | PRODUCTION SR MANAGER ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 |  | CENTRAL CONTROL BUILDING HVAC DB | CONFERENCE ROOM - SPLIT AC 1 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 |  | CENTRAL CONTROL BUILDING HVAC DB | CONFERENCE ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 |  | CENTRAL CONTROL BUILDING HVAC DB | CONFERENCE ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 |  | CENTRAL CONTROL BUILDING HVAC DB | DINING ROOM - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  | CENTRAL CONTROL BUILDING HVAC DB | SHIFT IN-CHARGE ROOM-SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.951 | 0 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 0 | YES | #DIV/0! | #DIV/0! | NA | NA | 0R x 0.6/1kV x 3C x 4 Sqmm | 0R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
306 |  | CENTRAL CONTROL BUILDING HVAC DB | WAITING HALL - SPLIT AC | CENTRAL CONTROL BUILDING |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 8.068 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 38 | 0 | 10 | 5 | 6 | 59 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8156 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 59 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 1 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 2 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 3 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 |  | CENTRAL CONTROL BUILDING HVAC DB | BATTERY ROOM - SPLIT AC 4 | CENTRAL CONTROL BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.951 | 18.8253 | 0 | 0.00 | 25 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 38 | 0 | 5 | 8 | 6 | 57 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7106 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 57 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 1422-ACDB-4-0002 | PDB-1 | HVAC DB-2 INCOMER | CENTRAL CONTROL BUILDING |  | INCOMER | 31.0737 | kW | 3Ph | 400 | 0.85 | 0.951 | 55.4863 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[33 empty] | 74524.5 | [15 empty] | #N/A |  | #N/A | [73 empty] | 719 | #N/A | #N/A | 697 | 3779 | 3584 | 95 | 21 | 515 | 3489 | 0 | 3196 | 3066 | 2037 | 991 | 763 | 0 | 293 | 293 | 194 | 114 | 179 | 0 |  | 0 | 179 | 0 | 857 | 86 | 86 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 744 | 229 | 0 | 0 | 229 | 196 | 0 | 51 | 36 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 600 | 1.438 | #N/A | #N/A | 1.394 | 7.558 | 7.168 | 0.19 | 0.042 | 1.03 | 6.978 | 0 | 6.392 | 6.132 | 4.074 | 1.982 | 1.526 | 0 | 0.586 | 0.586 | 0.388 |  | 0.358 | 0 |  | 0 | 0.358 | 0 | 1.714 | 0.172 | 0.172 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0 | 1.488 | 1.488 | 0.458 | 0 | 0 | 0.458 | 0.392 | 0 | 0.102 | 0.072 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 2 | #N/A | #N/A | 2 | 8 | 8 | 1 | 1 | 2 | 7 | 0 | 7 | 7 | 5 | 2 | 2 | 0 | 1 | 1 | 1 |  | 1 | 0 |  | 0 | 1 | 0 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 750 | 1.1504 | #N/A | #N/A | 1.1152 | 6.0464 | 5.7344 | 0.152 | 0.0336 | 0.824 | 5.5824 | 0 | 5.1136 | 4.9056 | 3.2592 | 1.5856 | 1.2208 | 0 | 0.4688 | 0.4688 | 0.3104 |  | 0.2864 | 0 |  | 0 | 0.2864 | 0 | 1.3712 | 0.1376 | 0.1376 | 0.0576 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1904 | 1.1904 | 0.3664 | 0 | 0 | 0.3664 | 0.3136 | 0 | 0.0816 | 0.0576 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0.024 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 2 | #N/A | #N/A | 2 | 7 | 6 | 1 | 1 | 1 | 6 | 0 | 6 | 5 | 4 | 2 | 2 | 0 | 1 | 1 | 1 |  | 1 | 0 |  | 0 | 1 | 0 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 900 | 0.95867 | #N/A | #N/A | 0.92933 | 5.0387 | 4.7787 | 0.12667 | 0.028 | 0.68667 | 4.652 | 0 | 4.2613 | 4.088 | 2.716 | 1.3213 | 1.0173 | 0 | 0.39067 | 0.39067 | 0.25867 |  | 0.23867 | 0 |  | 0 | 0.23867 | 0 | 1.1427 | 0.11467 | 0.11467 | 0.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0.992 | 0.992 | 0.30533 | 0 | 0 | 0.30533 | 0.0016 | 0 | 0.0016 | 0.0016 | 0.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016 | 0.0016 | 0 | 0.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 1 | #N/A | #N/A | 1 | 6 | 5 | 1 | 1 | 1 | 5 | 0 | 5 | 5 | 3 | 2 | 2 | 0 | 1 | 1 | 1 |  | 1 | 0 |  | 0 | 1 | 0 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## MV Cable sizing-6.6kV (hidden)
MV (6.6kV) CABLE SIZING
Sl. No | LOAD | [13 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  | CABLE DATA | [12 empty] | DERATING FACTOR | [5 empty] | CURRENT CARRYING CAPACITY |  |  | RUNNING CONDITION VOLTAGE DROP |  |  |  | MOTOR STARTING VOLTAGE DROP |  | Selected Cable Size
| Description | Unit | Equipment Location | Location As per Plot Plan | Type of feeder | Rated power | UNIT (kW / kVA) | 3Phase / 1Phase | Rated Voltage (V) | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard (kA) | Short circuit current withstand duration (sec) | Minimum size required for Short circuit withstand capacity (Sq.mm) | Installation | No. of Cores | Size in (Sq.mm) | Cable size | Cable size With (PE) Core | Cable Voltage (kV) | Current Rating of the Cable (A) | Cable resistance at 90°C (Ohm / Ph / km) | Cable reactance at 50Hz (Ohm / Ph / km) | Cable Length with in Electrical Building (m) | Cable Length from Electrical Building to Equipment (m) | Cable length both side dropping & Termination (m) | Cable length (m) | Ambient temperature (K1) | Grouping factor (K2) | Ground temperature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | Derated current carrying capacity (A) | No. of Runs | Derated current > Rated current | % VOLTAGE DROP DURING RUNNING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT (YES/NO) | (HIDE) | Maximum length under Allowable voltage drop | % VOLTAGE DROP DURING STARTING CONDITION | % VOLTAGE DROP WITHIN PERMISSIBLE LIMIT DURING STARTING CONDITION (YES/NO) | Selected cable size | Total Length in meters | No. of End Termination | Remarks | Dia of the conductor(mm) | Total Dia of the conductor(mm)
[37 empty] | A | [5 empty] | Meters
6.6kV MV Switchgear
1 | Incomer-1 from Unit Auxiliary Transformer (11/6.9kV)-1 | COMMON |  |  | I | 12500 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 1151.051 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 185 | 3C X 185 |  | 3.8/6.6 | 354 | 0.211 | 0.085 | 45 | 166 | 15 | 226 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 235.1622 | 5 | YES | 0.30602 | YES | 257.9811 | 6395817.978 | NA | NA | 5R x 0.6/1kV x 3C x 185 Sqmm | 1130 | 10 |  | 63 | 315 | 882
1a | Unit Auxiliary Transformer (11/6.9kV)-1 NGR | COMMON |  |  | I |  | kVA | 1Phase | 6600 | 0.85 | 0.95 | 400 | 0 | 0.00 | 0.3 | 10 | 6.6341 | AIR | 1C | 185 | 1C X 185 |  | 3.8/6.6 | 424 | 0.211 | 0.109 | 15 | 0 | 5 | 20 | 0.91 | 0.9 | NA | NA | NA | 0.819 | 347.256 | 2 | YES | 0.024854 | YES | 94.7077 | 6968808.4973 | NA | NA | 2R x 3.8/6.6kV x 1C x 185 Sqmm/Phase | 40 | 4 |  | 63 | 126
2 | Incomer-2 from Unit Auxiliary Transformer (11/6.9kV)-2 | COMMON |  |  | I | 12500 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 1151.051 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 185 | 3C X 185 |  | 3.8/6.6 | 354 | 0.211 | 0.085 | 45 | 206 | 15 | 266 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 235.1622 | 5 | YES | 0.36018 | YES | 257.9811 | 6395817.978 | NA | NA | 5R x 0.6/1kV x 3C x 185 Sqmm | 1330 | 10 |  | 63 | 315
2a | Unit Auxiliary Transformer (11/6.9kV)-2 NGR | COMMON |  |  | I |  | kVA | 1Phase | 6600 | 0.85 | 0.95 | 400 | 0 | 0.00 | 0.3 | 10 | 6.6341 | AIR | 1C | 185 | 1C X 185 |  | 3.8/6.6 | 424 | 0.211 | 0.109 | 15 | 0 | 5 | 20 | 0.91 | 0.9 | NA | NA | NA | 0.819 | 347.256 | 2 | YES | 0.024854 | YES | 94.7077 | 6968808.4973 | NA | NA | 2R x 3.8/6.6kV x 1C x 185 Sqmm/Phase | 40 | 4 |  | 63 | 126
3 | Incomer from BSDG 6.6kV Switchgear incomer-1 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 150 | 3C X 150 |  | 3.8/6.6 | 309 | 0.265 | 0.088 | 45 | 185 | 15 | 245 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 205.2687 | 2 | YES | 0.16081 | YES | 50.0213 | 13194368.4417 | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
4 | Incomer from BSDG 6.6kV Switchgear incomer-2 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 279.7203 | AIR | 3C | 150 | 3C X 150 |  | 3.8/6.6 | 309 | 0.265 | 0.088 | 45 | 185 | 15 | 245 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 205.2687 | 2 | YES | 0.16081 | YES | 50.0213 | 13194368.4417 | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
5 | Incomer from BSDG 6.6kV Switchgear incomer-3 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 111.8881 | AIR | 3C | 150 | 3C X 185 |  | 3.8/6.6 | 453 | 0.128 | 0.084 | 45 | 185 | 15 | 245 | 0.91 | 0.97 | NA | NA | NA | 0.8827 | 399.8631 | 2 | YES | 0.090615 | YES | 28.1869 | 23415139.8433 | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
6 | Incomer from BSDG 6.6kV Switchgear incomer-4 | COMMON |  |  | I | 2000 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 184.1682 | 0 | 0.00 | 40 | 1 | 111.8881 | AIR | 3C | 150 | 3C X 185 |  | 3.8/6.6 | 453 | 0.128 | 0.084 | 45 | 185 | 15 | 245 | 0.91 | 0.97 | NA | NA | NA | 0.8827 | 399.8631 | 2 | YES | 0.090615 | YES | 28.1869 | 23415139.8433 | NA | NA | 2R x 0.6/1kV x 3C x 150 Sqmm | 490 | 4 |  | 58 | 116
7 | CPP-Distribution Transformer-1 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.024442 | YES | 37.255 | 8857878.7796 | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
8 | CPP-Distribution Transformer-2 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.024442 | YES | 37.255 | 8857878.7796 | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
9 | CPP-Distribution Transformer-3 (6.6/0.42kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.024442 | YES | 37.255 | 8857878.7796 | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
10 | CPP-Distribution Transformer-4 (6.6/0.422kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.024442 | YES | 37.255 | 8857878.7796 | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
11 | CPP-Distribution Transformer-1 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 720 | kVA | 3Phase | 6600 | 0.86 | 1 | 55.11 | 0 | 0.00 | 0 | 0.16 | 0 | AIR | 3C | 185 | 3C X 185 |  | 3.8/6.6 | 354 | 0.723 | 0.084 | 15 | 0 | 10 | 225 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 76.56 | 1 | YES | 0.21628 | YES | 36.6286 | 9009360.886 | NA | NA | 1R x 0.6/1kV x 3C x 185 Sqmm | 225 | 2 |  | 56 | 56
12 | CPP-Distribution Transformer-2 (6.6/0.72kV) (GTG PMCC-690V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.024442 | YES | 37.255 | 8857878.7796 | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
13 | CPP-Distribution Transformer-3 (6.6/0.42kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.024442 | YES | 37.255 | 8857878.7796 | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
14 | CPP-Distribution Transformer-4 (6.6/0.42kV) (STG PMCC-400V) | COMMON |  |  | P | 1250 | kVA | 3Phase | 6600 | 0.85 | 0.95 | 115.1051 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.024442 | YES | 37.255 | 8857878.7796 | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
17 | CAPACITOR BANK FEEDER-1 | COMMON |  |  | P |  | kVA | 3Phase | 6600 | 0.85 | 0.95 | 0 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0 | YES | 0 | #DIV/0! | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
18 | CAPACITOR BANK FEEDER-2 | COMMON |  |  | P |  | kVA | 3Phase | 6600 | 0.85 | 0.95 | 0 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0 | YES | 0 | #DIV/0! | NA | NA | 1R x 0.6/1kV x 3C x 120 Sqmm | 25 | 2 |  | 56 | 56
11 | GT FUEL COMPRESSOR MOTOR-1 | COMMON | Fuel Gas receiving & metering station | 25 | M | 1601.5 | kW | 3Phase | 6600 | 0.85 | 0.95 | 173.4972 | 1040.9835 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 45 | 271 | 15 | 331 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.48778 | YES | 56.1542 | 5876675.7436 | 2.9267 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 331 | 2 |  | 56 | 56 | 336
12 | GT FUEL COMPRESSOR MOTOR-2 | COMMON | Fuel Gas receiving & metering station | 25 | M | 1601.5 | kW | 3Phase | 6600 | 0.85 | 0.95 | 173.4972 | 1040.9835 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 45 | 311 | 15 | 371 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.54673 | YES | 56.1542 | 5876675.7436 | 3.2804 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 371 | 2 |  | 56 | 56
13 | GT FUEL COMPRESSOR MOTOR-3 (STANDBY) | COMMON | Fuel Gas receiving & metering station | 25 | M | 1601.5 | kW | 3Phase | 6600 | 0.85 | 0.95 | 173.4972 | 1040.9835 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 45 | 311 | 15 | 371 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.54673 | YES | 56.1542 | 5876675.7436 | 3.2804 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 371 | 2 |  | 56 | 56
14 | HRSG FEED WATER PUMP-1 | COMMON | STG Building | 31 | M | 713.6 | kW | 3Phase | 6600 | 0.85 | 0.95 | 77.3073 | 463.8438 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 45 | 271 | 15 | 331 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.21735 | YES | 25.0213 | 13188755.8903 | 1.3041 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 331 | 2 |  | 56 | 56
15 | HRSG FEED WATER PUMP-2 | COMMON | STG Building | 31 | M | 713.6 | kW | 3Phase | 6600 | 0.85 | 0.95 | 77.3073 | 463.8438 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 45 | 271 | 15 | 331 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.21735 | YES | 25.0213 | 13188755.8903 | 1.3041 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 331 | 2 |  | 56 | 56
16 | HRSG WATER PUMP-3 (STANDBY) | COMMON | STG Building | 31 | M | 713.6 | kW | 3Phase | 6600 | 0.85 | 0.95 | 77.3073 | 463.8438 | 0.2 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 45 | 271 | 15 | 331 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 1 | YES | 0.21735 | YES | 25.0213 | 13188755.8903 | 1.3041 | YES | 1R x 0.6/1kV x 3C x 120 Sqmm | 331 | 2 |  | 56 | 56
19 | Load commutating invertor (SFC) | COMMON |  |  | P | 2388.092 | kW | 3Phase | 6600 | 0.85 | 1 | 245.7765 | 0 | 0.00 | 40 | 0.16 | 111.8881 | AIR | 3C | 120 | 3C X 120 |  | 3.8/6.6 | 274 | 0.325 | 0.09 | 15 | 0 | 10 | 25 | 0.91 | 0.73 | NA | NA | NA | 0.6643 | 182.0182 | 2 | YES | 0.026095 | YES | 79.5481 | 8296864.701 | NA | NA | 2R x 0.6/1kV x 3C x 120 Sqmm | 50 | 4 |  | 56 | 112
7066

## Catalogue A_old (hidden)
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 370 | 290 | 224 | 0.21 | 0.0875 | 26 | 400 | AIR | 1 | 0.9 | 0.66 | NA | NA | NA
1C X 240 | 445 | 340 | 283 | 0.16 | 0.0866 | 28 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 514 | 382 | 317 | 0.128 | 0.0857 | 31 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 605 | 437 | 370 | 0.1 | 0.0855 | 34 |  | Trench with cover | 1 | 0.81 | 0.78 | NA | NA | NA | 4 | 1.09 | 1.05
1C X 500 | 704 | 500 | 428 | 0.0774 | 0.0851 | 38 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 822 | 565 | 464 | 0.06 | 0.0843 | 42 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV (E) | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 62 | 70 | 57 | 3.94 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 79 | 90 | 75 | 2.44 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 108 | 117 | 99 | 1.54 | 0.0816 | 20 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 143 | 140 | 117 | 1.11 | 0.0794 | 21 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 173 | 168 | 143 | 0.82 | 0.0792 | 24 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 212 | 202 | 177 | 0.567 | 0.0752 | 27 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 257 | 243 | 217 | 0.41 | 0.0734 | 30
2C X 120 | 295 | 273 | 247 | 0.324 | 0.0726 | 32
2C X 150 | 342 | 310 | 305 | 0.264 | 0.0732 | 35
2C X 185 | 395 | 350 | 345 | 0.21 | 0.0727 | 39
2C X 240 | 465 | 401 | 393 | 0.16 | 0.0719 | 44
2C X 300 | 532 | 458 | 453 | 0.128 | 0.0711 | 48
2C X 400 | 622 | 505 | 553 | 0.1 | 0.0705 | 54
3-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16
3C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 19
3C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 19
3C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 21
3C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 23
3C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 26
3C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 30
3C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 33
3C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 35
3C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 39
3C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 43
3C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 48
3C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 53
3C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 59
4-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
4C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 21
3.5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 25
3.5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 27
3.5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 30
3.5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 36
3.5C X 95 | 221 | 198 | 168 | 0.41 | 0.0734 | 39
3.5C X 120 | 257 | 225 | 189 | 0.324 | 0.0726 | 43
3.5C X 150 | 293 | 252 | 210 | 0.264 | 0.0732 | 48
3.5C X 185 | 338 | 285 | 243 | 0.21 | 0.0727 | 53
3.5C X 240 | 401 | 330 | 282 | 0.16 | 0.0719 | 58
3.5C X 300 | 459 | 371 | 316 | 0.128 | 0.0711 | 64
3.5C X 400 | 536 | 423 | 282 | 0.1 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
5C X 10 | 60 | 57 | 48 | 3.94 | 0.0852 | 20
5C X 16 | 70 | 73 | 61 | 2.44 | 0.0815 | 20
5C X 25 | 95 | 96 | 80 | 1.54 | 0.0816 | 24
5C X 35 | 117 | 115 | 96 | 1.11 | 0.0794 | 26
5C X 50 | 141 | 134 | 116 | 0.82 | 0.0792 | 29
5C X 70 | 177 | 165 | 141 | 0.567 | 0.0752 | 33
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.125 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.12 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 324 | 252 | 240 | 0.325 | 0.115 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 368 | 281 | 267 | 0.265 | 0.114 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 424 | 317 | 303 | 0.211 | 0.109 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 502 | 367 | 350 | 0.161 | 0.105 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 577 | 414 | 397 | 0.13 | 0.102 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 673 | 470 | 451 | 0.102 | 0.098 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 757 | 519 | 493 | 0.08 | 0.096 | 46 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 876 | 586 | 557 | 0.063 | 0.094 | 50
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.09 | 54
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.088 | 58
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.097 | 49
3C X 95 | 238 | 24 | 180 | 0.411 | 0.093 | 52
3C X 120 | 274 | 232 | 206 | 0.325 | 0.09 | 56
3C X 150 | 309 | 259 | 231 | 0.265 | 0.088 | 58
3C X 185 | 354 | 293 | 262 | 0.211 | 0.085 | 63
3C X 240 | 415 | 338 | 304 | 0.162 | 0.083 | 69
3C X 300 | 472 | 380 | 343 | 0.13 | 0.082 | 75
3C X 400 | 545 | 432 | 393 | 0.102 | 0.08 | 84
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 6/10 (12)kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.125 | 27 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.12 | 29 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 324 | 252 | 240 | 0.325 | 0.115 | 30 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 368 | 281 | 267 | 0.265 | 0.114 | 33 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 424 | 317 | 303 | 0.211 | 0.109 | 34 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 502 | 367 | 350 | 0.161 | 0.105 | 36 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 577 | 414 | 397 | 0.13 | 0.102 | 39 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 673 | 470 | 451 | 0.102 | 0.098 | 42 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 757 | 519 | 493 | 0.08 | 0.096 | 46 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 876 | 586 | 557 | 0.063 | 0.094 | 50
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.09 | 54
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.088 | 59
Three core cable |  |  |  | 6/10 (12)kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.103 | 52
3C X 95 | 238 | 204 | 180 | 0.411 | 0.099 | 55
3C X 120 | 274 | 232 | 206 | 0.325 | 0.095 | 59
3C X 150 | 309 | 259 | 231 | 0.265 | 0.093 | 62
3C X 185 | 354 | 293 | 262 | 0.211 | 0.089 | 66
3C X 240 | 415 | 338 | 304 | 0.162 | 0.087 | 72
3C X 300 | 472 | 380 | 343 | 0.13 | 0.084 | 78
3C X 400 | 545 | 432 | 393 | 0.102 | 0.081 | 84
HV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 150mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1500 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.5 K.m/W) (K5) |  |  | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core | Single core | Single core | Multi core | Multi core
1C X 70 | 230 | 186 | 176 | 0.568 | 0.146 | 38 | 33000V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 280 | 221 | 210 | 0.411 | 0.14 | 39 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.95 | 120 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 120 | 324 | 252 | 240 | 0.325 | 0.134 | 41 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.96 | 150 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 150 | 368 | 281 | 267 | 0.265 | 0.132 | 43 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 185 | 424 | 317 | 303 | 0.211 | 0.126 | 45 | [8 empty] | 240 | 1.09 | 1.05 | 1.14 | 0.91 | 1.1 | 0.93
1C X 240 | 502 | 367 | 350 | 0.161 | 0.122 | 47 | [8 empty] | 300 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 300 | 577 | 414 | 397 | 0.13 | 0.118 | 50 | [8 empty] | 400 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 400 | 673 | 470 | 451 | 0.102 | 0.113 | 53 | [8 empty] | 500 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 500 | 757 | 519 | 493 | 0.08 | 0.109 | 56 | [8 empty] | 630 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 630 | 876 | 586 | 557 | 0.063 | 0.105 | 60
1C X 800 | 1005 | 655 | 622 | 0.051 | 0.101 | 65
1C X 1000 | 1138 | 723 | 687 | 0.043 | 0.099 | 69
Three core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 196 | 171 | 150 | 0.568 | 0.129 | 76
3C X 95 | 238 | 204 | 180 | 0.411 | 0.124 | 79
3C X 120 | 274 | 232 | 206 | 0.325 | 0.119 | 83
3C X 150 | 309 | 259 | 231 | 0.265 | 0.115 | 86
3C X 185 | 354 | 293 | 262 | 0.211 | 0.11 | 90
3C X 240 | 415 | 338 | 304 | 0.162 | 0.106 | 88
3C X 300 | 472 | 380 | 343 | 0.13 | 0.103 | 93
3C X 400 | 545 | 432 | 393 | 0.102 | 0.098 | 100

## Catalogue_CU (hidden)
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 479 | 370 | 315 | 0.127 | 0.0875 | 27 | 690/400V | AIR | 1 | 0.9 | 0.66 | NA | NA | NA
1C X 240 | 569 | 424 | 350 | 0.0965 | 0.0866 | 29 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 659 | 470 | 389 | 0.0769 | 0.0857 | 32 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 769 | 556 | 466 | 0.0602 | 0.0855 | 36 |  | Trench with cover | 1 | 0.81 | 0.78 | NA | NA | NA | 4 | 1.09 | 1.05
1C X 500 | 877 | 620 | 518 | 0.0468 | 0.0851 | 40 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 1013 | 695 | 555 | 0.0362 | 0.0843 | 44 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV (E) | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 82 | 90 | 75 | 2.34 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 113 | 114 | 95 | 1.47 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 148 | 147 | 124 | 0.93 | 0.081 | 21 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 186 | 177 | 152 | 0.671 | 0.0794 | 23 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 221 | 210 | 185 | 0.495 | 0.0792 | 25 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 278 | 260 | 228 | 0.319 | 0.0752 | 28 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 338 | 309 | 277 | 0.247 | 0.0734 | 32
2C X 120 | 402 | 351 | 300 | 0.196 | 0.0726 | 34
2C X 150 | 461 | 392 | 341 | 0.159 | 0.0732 | 37
2C X 185 | 527 | 448 | 384 | 0.127 | 0.072 | 42
2C X 240 | 607 | 509 | 434 | 0.0965 | 0.0719 | 47
2C X 300 | 688 | 579 | 495 | 0.0769 | 0.0711 | 51
2C X 400 | 818 | 638 | 553 | 0.0602 | 0.0705 | 57
3-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16
3C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 19
3C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 19
3C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 23
3C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 24
3C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 27
3C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 32
3C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 35
3C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 37
3C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 42
3C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 46
3C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 52
3C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 56
3C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 62
4-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 20
4C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 21
4C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 25
4C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 27
4C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 30
4C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 36
4C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 39
4C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 43
4C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 48
4C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 53
4C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 58
4C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 64
4C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902
5C X 10 | 66 | 72 | 60 | 2.34 | 0.0852
5C X 16 | 85 | 95 | 79 | 1.47 | 0.0815
5C X 25 | 122 | 122 | 100 | 0.93 | 0.081
5C X 35 | 148 | 146 | 120 | 0.671 | 0.0794
5C X 50 | 181 | 175 | 151 | 0.495 | 0.0792
5C X 70 | 230 | 212 | 182 | 0.319 | 0.0752
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.121 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.116 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 417 | 323 | 308 | 0.196 | 0.111 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 473 | 361 | 343 | 0.159 | 0.109 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 543 | 406 | 387 | 0.128 | 0.105 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 641 | 469 | 447 | 0.098 | 0.101 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 735 | 526 | 504 | 0.079 | 0.1 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 845 | 590 | 564 | 0.063 | 0.096 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 942 | 640 | 608 | 0.05 | 0.095 | 47 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.093 | 51
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.09 | 55
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.088 | 59
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.096 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.093 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.09 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.088 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.084 | 63
3C X 240 | 529 | 431 | 387 | 0.099 | 0.083 | 69
3C X 300 | 599 | 482 | 435 | 0.08 | 0.082 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.08 | 84
HV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 150mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1500 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.5 K.m/W) (K5) |  |  | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core | Single core | Single core | Multi core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.145 | 38 | 33000V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.139 | 40 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.95 | 120 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 120 | 417 | 323 | 308 | 0.196 | 0.133 | 41 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.96 | 150 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 150 | 473 | 361 | 343 | 0.159 | 0.132 | 44 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 185 | 543 | 406 | 387 | 0.128 | 0.126 | 46 | [8 empty] | 240 | 1.09 | 1.05 | 1.14 | 0.91 | 1.1 | 0.93
1C X 240 | 641 | 469 | 447 | 0.098 | 0.121 | 48 | [8 empty] | 300 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 300 | 735 | 526 | 504 | 0.079 | 0.118 | 50 | [8 empty] | 400 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 400 | 845 | 590 | 564 | 0.063 | 0.112 | 53 | [8 empty] | 500 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 500 | 942 | 640 | 608 | 0.05 | 0.108 | 57 | [8 empty] | 630 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.104 | 61
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.101 | 66
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.098 | 70
Three core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.129 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.123 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.118 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.115 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.11 | 63
3C X 240 | 529 | 431 | 387 | 0.99 | 0.105 | 69
3C X 300 | 599 | 482 | 435 | 0.8 | 0.103 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.098 | 84

## Catalogue Copper (hidden)
LV Cable Catalogue (KEC/RPG Make Catalogue Attached) | [7 empty] | DERATING FACTORS
1-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | LV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) 4 trafoil groups, 6 tier trays with Touching |  | Ground temperature (35°C) (K3) | Depth of laying (900 mm) (K4) |  | Thermal resistivity of ground (1.2 K.m/W) (K5)
| Air | Ground | Duct | [6 empty] | Single core (Trefoil Formation with Touching) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 185 | 479 | 370 | 315 | 0.127 | 0.0875 | 27 | 690/400V | AIR | 1 | 0.9 | 0.66 | NA | NA | NA
1C X 240 | 569 | 424 | 350 | 0.0965 | 0.0866 | 29 |  | Duct | NA | 0.74 | 0.71 | 0.96 | 0.98 | 0.98 | 1.5 | 1.09 | 1.05
1C X 300 | 659 | 470 | 389 | 0.0769 | 0.0857 | 32 |  | Ground | NA | 0.61 | 0.54 | 0.96 | 0.98 | 0.98 | 2.5 | 1.09 | 1.05
1C X 400 | 769 | 556 | 466 | 0.0602 | 0.0855 | 36 |  | Trench with cover | 1 | 0.81 | 0.78 | NA | NA | NA | 4 | 1.09 | 1.05
1C X 500 | 877 | 620 | 518 | 0.0468 | 0.0851 | 40 | [8 empty] | 6 | 1.09 | 1.05
1C X 630 | 1013 | 695 | 555 | 0.0362 | 0.0843 | 44 | [8 empty] | 10 | 1.09 | 1.06
[15 empty] | 16 | 1.09 | 1.06
2-core cable |  |  |  |  | 0.6/1.0 kV (E) | [9 empty] | 25 | 1.09 | 1.08
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia | [8 empty] | 35 | 1.09 | 1.08
| Air | Ground | Duct | [11 empty] | 50 | 1.09 | 1.08
2C X 1.5 | 29 | 33 | 29 | 15.5 | 0.108 | 12 | [8 empty] | 70 | 1.1 | 1.08
2C X 2.5 | 39 | 43 | 37 | 9.48 | 0.1007 | 13 | [8 empty] | 95 | 1.1 | 1.08
2C X 4 | 48 | 54 | 46 | 5.9 | 0.0947 | 14 | [8 empty] | 120 | 1.1 | 1.08
2C X 6 | 59 | 66 | 58 | 3.94 | 0.0902 | 15 | [8 empty] | 150 | 1.1 | 1.09
2C X 10 | 82 | 90 | 75 | 2.34 | 0.0852 | 17 | [8 empty] | 185 | 1.1 | 1.09
2C X 16 | 113 | 114 | 95 | 1.47 | 0.0815 | 18 | [8 empty] | 240 | 1.1 | 1.09
2C X 25 | 148 | 147 | 124 | 0.93 | 0.081 | 21 | [8 empty] | 300 | 1.1 | 1.09
2C X 35 | 186 | 177 | 152 | 0.671 | 0.0794 | 23 | [8 empty] | 400 | 1.11 | 1.1
2C X 50 | 221 | 210 | 185 | 0.495 | 0.0792 | 25 | [8 empty] | 500 | 1.11 | 1.1
2C X 70 | 278 | 260 | 228 | 0.319 | 0.0752 | 28 | [8 empty] | 630 | 1.11 | 1.1
2C X 95 | 338 | 309 | 277 | 0.247 | 0.0734 | 32
2C X 120 | 402 | 351 | 300 | 0.196 | 0.0726 | 34
2C X 150 | 461 | 392 | 341 | 0.159 | 0.0732 | 37
2C X 185 | 527 | 448 | 384 | 0.127 | 0.072 | 42
2C X 240 | 607 | 509 | 434 | 0.0965 | 0.0719 | 47
2C X 300 | 688 | 579 | 495 | 0.0769 | 0.0711 | 51
2C X 400 | 818 | 638 | 553 | 0.0602 | 0.0705 | 57
3-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
3C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
3C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 14
3C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 15
3C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 16
3C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 19
3C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 19
3C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 23
3C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 24
3C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 27
3C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 32
3C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 35
3C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 37
3C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 42
3C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 46
3C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 52
3C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 56
3C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 62
4-core cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
4C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108 | 13
4C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007 | 15
4C X 4 | 38 | 44 | 37 | 5.9 | 0.0947 | 16
4C X 6 | 51 | 55 | 46 | 3.94 | 0.0902 | 18
4C X 10 | 66 | 72 | 60 | 2.34 | 0.0852 | 20
4C X 16 | 85 | 95 | 79 | 1.47 | 0.0815 | 21
4C X 25 | 122 | 122 | 100 | 0.93 | 0.081 | 25
4C X 35 | 148 | 146 | 120 | 0.671 | 0.0794 | 27
4C X 50 | 181 | 175 | 151 | 0.495 | 0.0792 | 30
4C X 70 | 230 | 212 | 182 | 0.319 | 0.0752 | 36
4C X 95 | 284 | 253 | 211 | 0.247 | 0.0734 | 39
4C X 120 | 330 | 290 | 236 | 0.196 | 0.0726 | 43
4C X 150 | 375 | 325 | 271 | 0.159 | 0.0732 | 48
4C X 185 | 431 | 362 | 308 | 0.127 | 0.072 | 53
4C X 240 | 512 | 418 | 257 | 0.0965 | 0.0719 | 58
4C X 300 | 582 | 467 | 406 | 0.0769 | 0.0711 | 64
4C X 400 | 661 | 518 | 439 | 0.0602 | 0.0705 | 72
5-Core Cable |  |  |  |  | 0.6/1.0 kV (E)
Size in mm2 | Current carrying capacity |  |  | AC Resistance Ohm/km 90°C | Reactance Ohm/km | Cable Dia
| Air | Ground | Duct
5C X 1.5 | 22 | 25 | 22 | 15.5 | 0.108
5C X 2.5 | 28 | 34 | 28 | 9.48 | 0.1007
5C X 4 | 38 | 44 | 37 | 5.9 | 0.0947
5C X 6 | 51 | 55 | 46 | 3.94 | 0.0902
5C X 10 | 66 | 72 | 60 | 2.34 | 0.0852
5C X 16 | 85 | 95 | 79 | 1.47 | 0.0815
5C X 25 | 122 | 122 | 100 | 0.93 | 0.081
5C X 35 | 148 | 146 | 120 | 0.671 | 0.0794
5C X 50 | 181 | 175 | 151 | 0.495 | 0.0792
5C X 70 | 230 | 212 | 182 | 0.319 | 0.0752
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.121 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.116 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 417 | 323 | 308 | 0.196 | 0.111 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 473 | 361 | 343 | 0.159 | 0.109 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 543 | 406 | 387 | 0.128 | 0.105 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 641 | 469 | 447 | 0.098 | 0.101 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 735 | 526 | 504 | 0.079 | 0.1 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 845 | 590 | 564 | 0.063 | 0.096 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 942 | 640 | 608 | 0.05 | 0.095 | 47 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.093 | 51
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.09 | 55
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.088 | 59
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.096 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.093 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.09 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.088 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.084 | 63
3C X 240 | 529 | 431 | 387 | 0.099 | 0.083 | 69
3C X 300 | 599 | 482 | 435 | 0.08 | 0.082 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.08 | 84
MV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 200mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1200 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.2 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.121 | 26 | 6600V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.116 | 27 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.97 | 120 | 1.09 | 1.05
1C X 120 | 417 | 323 | 308 | 0.196 | 0.111 | 29 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.95 | 0.96 | 150 | 1.09 | 1.05
1C X 150 | 473 | 361 | 343 | 0.159 | 0.109 | 30 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05
1C X 185 | 543 | 406 | 387 | 0.128 | 0.105 | 33 | [8 empty] | 240 | 1.09 | 1.05
1C X 240 | 641 | 469 | 447 | 0.098 | 0.101 | 35 | [8 empty] | 300 | 1.09 | 1.05
1C X 300 | 735 | 526 | 504 | 0.079 | 0.1 | 38 | [8 empty] | 400 | 1.09 | 1.05
1C X 400 | 845 | 590 | 564 | 0.063 | 0.096 | 41 | [8 empty] | 500 | 1.09 | 1.05
1C X 500 | 942 | 640 | 608 | 0.05 | 0.095 | 47 | [8 empty] | 630 | 1.09 | 1.05
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.093 | 51
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.09 | 55
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.088 | 59
Three core cable |  |  |  | 3.8/6.6 kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.096 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.093 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.09 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.088 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.084 | 63
3C X 240 | 529 | 431 | 387 | 0.099 | 0.083 | 69
3C X 300 | 599 | 482 | 435 | 0.08 | 0.082 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.08 | 84
HV Cable Catalogue (KEC/RPG Make Catalogue Attached)
Single core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia | MV | XLPE | Ambient temperature (40°C) (K1) | Grouping factor (K2) Duct Spacing (3 cables) 150mm Centre to Centre & 3 tier trays with spacing |  | Ground temperature (35°C) (K3) | Depth of laying (1500 mm) (K4) |  | Thermal resistivity of ground buried in Duct (1.5 K.m/W) (K5) |  |  | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (1.0 K.m/W) (K5) | Thermal resistivity of ground buried in Duct (2.0 K.m/W) (K5)
| Air (Trefoil) | Ground (Trefoil) | Duct (Trefoil) | [6 empty] | Single core (Trefoil Formation with 150mm spacing) | Multi core (Touching) |  | Single core | Multi core | Cable Size | Single core | Multi core | Single core | Single core | Multi core | Multi core
1C X 70 | 296 | 239 | 227 | 0.342 | 0.145 | 38 | 33000V | AIR | 0.91 | 0.9 | 0.97 | NA | NA | NA
1C X 95 | 361 | 285 | 271 | 0.247 | 0.139 | 40 |  | Duct | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.95 | 120 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 120 | 417 | 323 | 308 | 0.196 | 0.133 | 41 |  | Ground | NA | 0.64 | 0.8 | 0.89 | 0.93 | 0.96 | 150 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 150 | 473 | 361 | 343 | 0.159 | 0.132 | 44 |  | Trench with cover | 0.91 | 0.9 | 0.97 | NA | NA | NA | 185 | 1.09 | 1.05 | 1.13 | 0.91 | 1.09 | 0.93
1C X 185 | 543 | 406 | 387 | 0.128 | 0.126 | 46 | [8 empty] | 240 | 1.09 | 1.05 | 1.14 | 0.91 | 1.1 | 0.93
1C X 240 | 641 | 469 | 447 | 0.098 | 0.121 | 48 | [8 empty] | 300 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 300 | 735 | 526 | 504 | 0.079 | 0.118 | 50 | [8 empty] | 400 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 400 | 845 | 590 | 564 | 0.063 | 0.112 | 53 | [8 empty] | 500 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 500 | 942 | 640 | 608 | 0.05 | 0.108 | 57 | [8 empty] | 630 | 1.09 | 1.05 | 1.14 | 0.9 | 1.1 | 0.92
1C X 630 | 1071 | 712 | 676.4 | 0.041 | 0.104 | 61
1C X 800 | 1210 | 781 | 741.95 | 0.034 | 0.101 | 66
1C X 1000 | 1332 | 841 | 798.95 | 0.029 | 0.098 | 70
Three core cable |  |  |  | 18/30 (36) kV
Size in mm2 | Current carrying capacity |  |  | Approx. A.C. Resistance at 90°C Ohm/km | Approx. Reactance Ohm/km | Nominal Dia
| Air | Ground | Duct
3C X 70 | 253 | 220 | 194 | 0.342 | 0.129 | 49
3C X 95 | 307 | 263 | 232 | 0.247 | 0.123 | 52
3C X 120 | 352 | 298 | 264 | 0.196 | 0.118 | 56
3C X 150 | 397 | 332 | 296 | 0.159 | 0.115 | 58
3C X 185 | 453 | 374 | 335 | 0.128 | 0.11 | 63
3C X 240 | 529 | 431 | 387 | 0.99 | 0.105 | 69
3C X 300 | 599 | 482 | 435 | 0.8 | 0.103 | 75
3C X 400 | 683 | 541 | 492 | 0.064 | 0.098 | 84

## Tray-Void (hidden)
APCh-CPP-CABLE TRAY BOQ
[6 empty] | Inside Electrical room-Cable celler (GF) | [6 empty] | Inside Electrical room-Cable celler (SF) |  |  |  | For outside rack upto electrical room - north side | [9 empty] | For outside rack upto electrical room - north side to south side rack upto HRSG | [5 empty] | from Rack to BSDG Building
Voltage | Tray Type | Tray size | NOS | no. of motors | Purpose | Inside electrical room cable cellar (below GTG Panel) | Inside electrical room cable cellar (below STG Panel) | Inside electrical room cable cellar (below 6.6kv Panel) | Inside electrical room cable cellar CROSSING (below 6.6kv Panel) | Inside electrical room cable cellar (below 33kv Panel) | Inside electrical room cable cellar Crossing (below 33kv Panel) | Battery room side | Inside electrical room 2nd floor cable cellar (below 150kv Panel) | Inside electrical room dropper (below 150kv Panel) | Inside electrical room 2nd floor cable cellar (150kv Control) | raiser & droppers | from electrical building edge to north side pipe rack connecting | Rack on front side Electrical building | from electrical building edge to north side pipe rack connecting | from north side pipe rack to north & south side pipe rack connectivity | from north & south side pipe rack to GTG -1 Electrical room crossing | from north side pipe to crossing towards GTG -1 side to Electrical room (GTG-1) | from pipe rack crossing GTG -1 side to GTG-2 crossing pipe rack | from crossing pipe rack towards GTG -2 side to Electrical room (GTG-2) | crossing from celler to STG | Crossing from rack to STG package | from north side pipe rack to south side side pipe rack connectivity towards HRSG-1 side | from north side pipe rack to STG Pckage | from south side side pipe rack connectivity towards HRSG-1 | from south side side pipe rack crossing to HRSG-1 area | From South side HRSG - to HRSG-2 crossing | from south side side pipe rack crossing HRSG-2 to HRSG area | from north side pipe rack to BSDG Building | from Rack to inside building | dropping near equipment | Total Quantity
Route no. | [5 empty] | EB-1 | EB-2 | EB-3 | EB-3A | EB-4 | EB-4A | EB-4B+C | EB-5 | EB-5A | EB-5B |  | OSN-1 | OSN-2 | OSN-3 | OSN-4 | OSN-5 | OSN-6 | OSN-7 | OSN-8 | OSN-8A | OSN-8B | OSS-1 | OSS-1A | OSS-2 | OSS-3 | OSS-4 | OSS-5 | OSB-1 | OSB-2
Length | [5 empty] | 43 | 43 | 34 | 11 | 34 | 6 | 20 | 23 | 10 | 34 | 20 | 12 | 15 | 12 | 32 | 45 | 26 | 40 | 26 | 15 | 25 | 105 | 35 | 26 | 36 | 40 | 36 | 115 | 15 | 3
Purpose | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cable Trays for Electrical Power Cable
150kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
150kV-P | Ladder | L-600 | 1 |  | GSUT | [7 empty] | 23 | 10 |  | 20 |  |  | 12 | 32 | 45 |  | 40 | [11 empty] | 0 | 182
150kV-P | Ladder | L-300 | 1 | [12 empty] | 20 | [5 empty] | 26 |  | 26 | [10 empty] | 0 | 72
150kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
150kV-P | Ladder | L-150 | 1 | 2 | GSUT | [29 empty] | 6 | 6
150kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
[35 empty] | 0 | 0
33kV-P | Ladder | L-600 | 2 | [6 empty] | 68 | 12 | [23 empty] | 0 | 80
33kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
33kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
6.6kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
6.6kV-P | Ladder | L-600 | 1 | [31 empty] | 0 | 0
6.6kV-P | Ladder | L-600 | 1 |  | 6.6kv Incoming-BSDG |  |  | 34 | 11 | [6 empty] | 20 | 12 | 15 | 12 | 32 | [12 empty] | 105 | 26 | 0 | 267
6.6kV-P | Ladder | L-600 | 1 |  | 6.6kv motors |  |  | 34 | 11 | [6 empty] | 20 | 12 | 15 | 12 | 32 | [14 empty] | 0 | 136
6.6kV-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
6.6kV-P | Ladder | L-300 | 1 | [12 empty] | 20 | [5 empty] | 26 |  | 26 | [10 empty] | 0 | 72
6.6kV-P | Ladder | L-150 | 1 | 6 | [30 empty] | 18 | 18
6.6kV-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
LV GTG-P | Ladder | L-600 | 2 |  | GTG Panels | 86 | [9 empty] | 40 |  | 24 | 64 | 90 | 52 | [13 empty] | 0 | 356
LV GTG-P | Ladder | L-600 | 1 | [12 empty] | 20 | [5 empty] | 40 | 26 | 26 | [10 empty] | 0 | 112
LV GTG-P | Ladder | L-300 | 1 | 4 | [30 empty] | 12 | 12
LV GTG-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
LV GTG-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
LV GTG-P | Ladder | L-150 | 1 | [31 empty] | 0 | 0
[35 empty] | 0 | 0
LV STG-P | Ladder | L-600 | 3 |  | STG Motors |  | 129 | [27 empty] | 0 | 129
LV STG-P | Ladder | L-600 | 2 | [12 empty] | 40 | 24 | 30 | 24 | 64 | [7 empty] | 70 | [6 empty] | 0 | 252
LV STG-P | Ladder | L-600 | 1 | [12 empty] | 20 | [8 empty] | 15 | 25 | [8 empty] | 0 | 60
LV STG-P | Ladder | L-300 | 1 | [12 empty] | 20 | [8 empty] | 15 | 25 | [8 empty] | 0 | 60
LV STG-P | Ladder | L-300 | 1 | [31 empty] | 0 | 0
LV STG-P | Ladder | L-150 | 1 | 23 | Droppets | [29 empty] | 69 | 69
LV STG-P | Ladder | L-150 | 1 | 41 | [30 empty] | 123 | 123
[35 empty] | 0 | 0
Cable Trays for Electrical control Cable
LV -C | Perforated | P-600 | 1 |  |  | 43 | 43 | 34 | 11 | 34 | 6 |  | 23 | 10 | 34 | 20 | 12 | 15 | 12 | 32 | 45 |  | 40 | 26 |  |  |  | 35 | [6 empty] | 0 | 475
LV -C | Perforated | P-300 | 1 | [5 empty] | 11 |  | 6 | 20 |  |  |  | 20 | [5 empty] | 26 |  | 26 | 15 | 25 | 105 |  | 26 | 36 | 40 | 36 | 115 | 15 | 0 | 522
LV -C | Perforated | P-300 | 1 | [31 empty] | 0 | 0
LV -C | Perforated | P-150 | 1 | [8 empty] | 20 | [9 empty] | 26 |  | 26 | [10 empty] | 0 | 72
LV -C | Perforated | P-150 | 1 | [31 empty] | 0 | 0
3075
Tray Type |  | Size | Quantity in Mtrs | Quantity with 5% margin in Mtrs | Horizontal Bends (Nos) | Vertical Bends (Nos) | Tee Bends (Nos) | Reducer (Nos) |  | Tray Support C-CHANNEL: (75*40*40*6)mm Mtrs | Tray Support ANGLE: (50*50*6)mm mtrs
Ladder Type Cable Tray |  | L-600 | 1574 | 1653 | 78.7 | 47.22 | 47.22 | 47.22 |  | 794 | 218
Ladder Type Cable Tray |  | L-300 | 216 | 227 | 10.8 | 6.48 | 6.48 | 6.48
Ladder Type Cable Tray |  | L-150 | 216 | 227 | 10.8 | 6.48 | 6.48
Perforated Type Cable Tray |  | P-600 | 475 | 499 | 23.75 | 14.25 | 14.25 | 14.25
Perforated Type Cable Tray |  | P-300 | 522 | 549 | 26.1 | 15.66 | 15.66 | 15.66
Perforated Type Cable Tray |  | P-150 | 72 | 76 | 3.6 | 2.16 | 2.16
Perforated Type Cable Tray -Cover |  | P-600 | 475 | 499 |  |  |  | 14.25
Perforated Type Cable Tray -Cover |  | P-300 | 459 | 482 |  |  |  | 13.77

## requred Dia (hidden)
BSDG
| inside | outside | outside | outside | outside
GTG requred | 1200mm | 1200 | 600 | 600
STG requred | 1800mm | 1800 | 900 | 900
6.6kv | 1200 | 600 | 300 | 300 | 600
33kV | 1200
150kV | 600 | 600 | 300 | 300

## LV Cable sizing_SS-2
LV POWER CABLE SIZING
Sl. No |  |  | LOAD | [12 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  | CABLE DATA | [14 empty] | DERATING FACTOR | [5 empty] | CURRENT CARRYING CAPACITY |  |  | RUNNING CONDITION VOLTAGE DROP |  | MOTOR STARTING VOLTAGE DROP |  | Selected Cable Size
| Tag No. | From | Description | Equipment Location | Bus | Type of feeder | Rated power | UNIT (kW / kVa) | 3Phase / 1Phase | Rated Voltage (V) | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard (ka) | Short circuit current withstand duration (sec) | Minimum size required for Short circuit withstand capacity (Sq.mm) | Installation | No. of Cores | Size in (Sq.mm) | Cable size | Cable size With (PE) Core | Cable Voltage (kV) | Current Rating of the Cable (a) | Cable resistance at 90°C (Ohm / Ph / km) | Cable reactance at 50Hz (Ohm / Ph / km) | Cable Length with in Electrical Building (m) | Cable Length from Electrical Building to Equipment (m) | Cable length Riser & Dropper (m) | Cable length both side dropping & Termination (m) | Spare 10% | Cable length for each run (m) | ambient temperature (K1) | Grouping factor (K2) | Ground temperature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | Derated current carrying capacity (a) | No. of Runs | Derated current > Rated current | % VOLTaGE DROP DURING RUNNING CONDITION | % VOLTaGE DROP WITHIN PERMISSIBLE LIMIT (YES/NO) | % VOLTAGE DROP DURING STaRTING CONDITION | % VOLTaGE DROP WITHIN PERMISSIBLE LIMIT DURING STaRTING CONDITION (YES/NO) | Selected cable size | Selected cable size | Total Cable Length in meters | Remarks | No. of End Termination | Cable Route(Sections) | Dia of the conductor(mm) | Total Dia of the conductor (mm) | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | I.A | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | TA | T1.A | U |  | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | I.A | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | TA | T1.A | U
|  |  | COOLING TOWER SUBSTATION | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | PMCC-2 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | FIRE SYSTEM | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1418-P1001A | PMCC-2 | JOCKEY PUMP-1 | FIRE WATER PUMP HOUSE | A | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 22 | 104.4 | 8 | 5 | 14 | 153.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.5177 | YES | 6.0055 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 153.4 |  | 2 | Q4Q5Q6Q7Q8 | 33 | 33 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | - | PMCC-2 | JOCKEY PUMP-1-SPACE HEATER | FIRE WATER PUMP HOUSE | A | POWER | 0.12 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.2145 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 104.4 | 8 | 5 | 14 | 153.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.11557 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 153.4 |  | 2 | Q4Q5Q6Q7Q8 | 14 | 14 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1418-P002A | PMCC-2 | JOCKEY PUMP-2 | FIRE WATER PUMP HOUSE | B | MOTOR | 55 | kW | 3Ph | 400 | 0.85 | 0.954 | 97.9011 | 587.4065 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 12 | 104.4 | 8 | 5 | 13 | 142.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.3372 | YES | 5.5749 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 142.4 |  | 2 | Q4Q5Q6Q7Q8 | 33 | 33 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | - | PMCC-2 | JOCKEY PUMP-2-SPACE HEATER | FIRE WATER PUMP HOUSE | B | POWER | 0.12 | kW | 3Ph | 400 | 0.85 | 0.95 | 0.2145 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 104.4 | 8 | 5 | 13 | 142.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.10728 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 142.4 |  | 2 | Q4Q5Q6Q7Q8 | 14 | 14 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1418-P003A | PMCC-2 | MAIN FIRE PUMP - 1 (230V) | FIRE WATER PUMP HOUSE | A | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.954 | 26.8086 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 22 | 104.4 | 8 | 5 | 14 | 153.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.2878 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 153.4 |  | 2 | Q4Q5Q6Q7Q8 | 26 | 26 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1418-P004A | PMCC-2 | MAIN FIRE PUMP - 2 (230V) | FIRE WATER PUMP HOUSE | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.954 | 26.8086 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 12 | 104.4 | 8 | 5 | 13 | 142.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.1237 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 142.4 |  | 2 | Q4Q5Q6Q7Q8 | 26 | 26 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1418-P005A | PMCC-2 | STANDBY FIRE PUMP - 1 (230V) | FIRE WATER PUMP HOUSE | A | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.954 | 26.8086 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 22 | 104.4 | 8 | 5 | 14 | 153.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.2878 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 153.4 |  | 2 | Q4Q5Q6Q7Q8 | 26 | 26 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1418-P006A | PMCC-2 | STANDBY FIRE PUMP - 2 (230V) | FIRE WATER PUMP HOUSE | B | POWER | 5 | kW | 1Ph | 230 | 0.85 | 0.954 | 26.8086 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 50 | 3C X 50 | 3C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 12 | 104.4 | 8 | 5 | 13 | 142.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.1237 | YES | NA | NA | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50 Sqmm | 142.4 |  | 2 | Q4Q5Q6Q7Q8 | 26 | 26 | [49 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Cooling Tower package | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1407-PK-001A | PMCC-2 | COOLING TOWER FAN - A | COOLING TOWER AREA | A | MOTOR | 200 | kW | 3Ph | 400 | 0.86 | 0.964 | 348.2143 | 2089.2859 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 22 | 95 | 8 | 5 | 13 | 143 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 2 | YES | 2.347 | YES | 7.3244 | YES | 2R x 0.6/1kV x 3C x 185 Sqmm | 2R x 0.6/1kV x 3C x 185+PE Sqmm | 286 |  | 4 | Q3RR1R1.A | 43 | 86 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 86 | 86 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | - | PMCC-2 | COOLING TOWER FAN - A-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.12 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.64612 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 95 | 10 | 8 | 13 | 138 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.54463 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 138 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1407-PK-001B | PMCC-2 | COOLING TOWER FAN - B | COOLING TOWER AREA | B | MOTOR | 200 | kW | 3Ph | 400 | 0.86 | 0.964 | 348.2143 | 2089.2859 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 12 | 109 | 8 | 5 | 14 | 148 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 2 | YES | 2.429 | YES | 7.5805 | YES | 2R x 0.6/1kV x 3C x 185 Sqmm | 2R x 0.6/1kV x 3C x 185+PE Sqmm | 296 |  | 4 | Q3RR1R1.A | 43 | 86 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 86 | 86 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | - | PMCC-2 | COOLING TOWER FAN - B-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.12 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.64612 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 109 | 10 | 8 | 14 | 153 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.60383 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 153 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 1407-PK-001C | PMCC-2 | COOLING TOWER FAN - C | COOLING TOWER AREA | A | MOTOR | 200 | kW | 3Ph | 400 | 0.86 | 0.964 | 348.2143 | 2089.2859 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 22 | 123 | 8 | 5 | 16 | 174 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 2 | YES | 2.8558 | YES | 8.9122 | YES | 2R x 0.6/1kV x 3C x 185 Sqmm | 2R x 0.6/1kV x 3C x 185+PE Sqmm | 348 |  | 4 | Q3RR1R1.A | 43 | 86 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 86 | 86 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | - | PMCC-2 | COOLING TOWER FAN - C-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.12 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.64612 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 123 | 10 | 8 | 16 | 169 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.66697 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 169 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 1407-PK-001D | PMCC-2 | COOLING TOWER FAN - D | COOLING TOWER AREA | B | MOTOR | 200 | kW | 3Ph | 400 | 0.86 | 0.964 | 348.2143 | 2089.2859 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 185 | 3C X 185 | 3C X 185+PE | 0.6/1.0 | 338 | 0.21 | 0.0727 | 12 | 137 | 8 | 5 | 17 | 179 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 198.5412 | 2 | YES | 2.9378 | YES | 9.1683 | YES | 2R x 0.6/1kV x 3C x 185 Sqmm | 2R x 0.6/1kV x 3C x 185+PE Sqmm | 358 |  | 4 | Q3RR1R1.A | 43 | 86 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 86 | 86 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | - | PMCC-2 | COOLING TOWER FAN - D-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.12 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.64612 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 137 | 10 | 8 | 17 | 184 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.72617 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 184 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 1407-PK-001E | PMCC-2 | COOLING TOWER FAN - E | COOLING TOWER AREA | A | MOTOR | 200 | kW | 3Ph | 400 | 0.86 | 0.964 | 348.2143 | 2089.2859 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 240 | 3C X 240 | 3C X 240+PE | 0.6/1.0 | 401 | 0.16 | 0.0719 | 22 | 151 | 8 | 5 | 19 | 205 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 2 | YES | 2.6937 | YES | 9.5 | YES | 2R x 0.6/1kV x 3C x 240 Sqmm | 2R x 0.6/1kV x 3C x 240+PE Sqmm | 410 |  | 4 | Q3RR1R1.A | 48 | 96 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 96 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | - | PMCC-2 | COOLING TOWER FAN - E-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.12 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.64612 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 151 | 10 | 8 | 19 | 200 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.78932 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 200 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 1407-PK-001F | PMCC-2 | COOLING TOWER FAN - F | COOLING TOWER AREA | B | MOTOR | 200 | kW | 3Ph | 400 | 0.86 | 0.964 | 348.2143 | 2089.2859 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 240 | 3C X 240 | 3C X 240+PE | 0.6/1.0 | 401 | 0.16 | 0.0719 | 12 | 165 | 8 | 5 | 19 | 209 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 2 | YES | 2.7462 | YES | 9.6854 | YES | 2R x 0.6/1kV x 3C x 240 Sqmm | 2R x 0.6/1kV x 3C x 240+PE Sqmm | 418 |  | 4 | Q3RR1R1.A | 48 | 96 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 96 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | - | PMCC-2 | COOLING TOWER FAN - F-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.12 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.64612 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 165 | 10 | 8 | 20 | 215 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.84851 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 215 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 1407-PK-001G | PMCC-2 | COOLING TOWER FAN - G | COOLING TOWER AREA | A | MOTOR | 200 | kW | 3Ph | 400 | 0.86 | 0.964 | 348.2143 | 2089.2859 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 240 | 3C X 240 | 3C X 240+PE | 0.6/1.0 | 401 | 0.16 | 0.0719 | 22 | 179 | 8 | 5 | 22 | 228 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 235.5474 | 2 | YES | 2.9959 | YES | 10.5658 | YES | 2R x 0.6/1kV x 3C x 240 Sqmm | 2R x 0.6/1kV x 3C x 240+PE Sqmm | 456 |  | 4 | Q3RR1R1.A | 48 | 96 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 96 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | - | PMCC-2 | COOLING TOWER FAN - G-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.12 | kW | 1Ph | 230 | 0.85 | 0.95 | 0.64612 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 179 | 10 | 8 | 21 | 230 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.90771 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 230 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | - | PMCC-2 | SSF FEED PUMP- A | COOLING TOWER AREA | A | MOTOR | 22 | kW | 3Ph | 400 | 0.84 | 0.944 | 40.0464 | 240.2784 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.9542 | YES | 3.8711 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm | 154 |  | 2 | Q3RR1R1.A | 26 | 26 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | - | PMCC-2 | SSF FEED PUMP- A-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 154 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | - | PMCC-2 | SSF FEED PUMP- B | COOLING TOWER AREA | B | MOTOR | 22 | kW | 3Ph | 400 | 0.84 | 0.944 | 40.0464 | 240.2784 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 12 | 100 | 10 | 8 | 13 | 143 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.8146 | YES | 3.5946 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm | 143 |  | 2 | Q3RR1R1.A | 26 | 26 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | - | PMCC-2 | SSF FEED PUMP- B-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 100 | 10 | 8 | 13 | 143 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.9406 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 143 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | - | PMCC-2 | SSF FEED PUMP- C | COOLING TOWER AREA | A | MOTOR | 22 | kW | 3Ph | 400 | 0.85 | 0.954 | 39.1604 | 234.9626 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 50 | 3C X 50 | 3C X 50+PE | 0.6/1.0 | 141 | 0.82 | 0.0792 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 1.9291 | YES | 3.7854 | YES | 1R x 0.6/1kV x 3C x 50 Sqmm | 1R x 0.6/1kV x 3C x 50+PE Sqmm | 154 |  | 2 | Q3RR1R1.A | 26 | 26 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | - | PMCC-2 | SSF FEED PUMP- C-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 154 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | - | PMCC-2 | SSF BACKWASH PUMP- A | COOLING TOWER AREA | A | MOTOR | 30 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.3787 | YES | 3.2886 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 154 |  | 2 | Q3RR1R1.A | 33 | 33 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | - | PMCC-2 | SSF BACKWASH PUMP- A-SPACE HEATER | COOLING TOWER AREA | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 154 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | - | PMCC-2 | SSF BACKWASH PUMP- B | COOLING TOWER AREA | B | MOTOR | 30 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 95 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 12 | 100 | 10 | 8 | 13 | 143 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.2802 | YES | 3.0537 | YES | 1R x 0.6/1kV x 3C x 95 Sqmm | 1R x 0.6/1kV x 3C x 95+PE Sqmm | 143 |  | 2 | Q3RR1R1.A | 33 | 33 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | - | PMCC-2 | SSF BACKWASH PUMP- B-SPACE HEATER | COOLING TOWER AREA | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 12 | 100 | 10 | 8 | 13 | 143 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 0.9406 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 143 |  | 2 | Q3RR1R1.A | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | - | PMCC-2 | SSF BACKWASH PUMP- A | COOLING TOWER AREA | A | MOTOR | 15 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.3787 | YES | 3.2886 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 154 |  | 2 |  | 33 | 33
34 | - | PMCC-2 | SSF BACKWASH PUMP- A | COOLING TOWER AREA | A | MOTOR | 15 | kW | 3Ph | 400 | 0.85 | 0.954 | 53.4006 | 320.4036 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 95 | 3C X 95+PE | 0.6/1.0 | 221 | 0.41 | 0.0734 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.3787 | YES | 3.2886 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 154 |  | 2 |  | 33 | 33
|  |  | Cooling Tower package | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PMCC-2 | MOV ON COOLING WATER BYPASS LINE | COOLING TOWER AREA | B | MOTOR | 1 | kW | 3Ph | 400 | 0.8 | 0.841 | 2.1454 | 12.8723 | 0.2 | 50 | 0 | 0 | TRENCH | 3.5C | 4 | 3.5C X 4 | 3.5C X 4+PE | 0.6/1.0 | #N/A | #N/A | #N/A | 12 | 100 | 10 | 8 | 13 | 143 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | Chemical dosing for CT package | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 1407-PM-121 A | PMCC-2 | ANTISCALANT DOING PUMP A | COOLING TOWER AREA | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 22 | 36.4 | 20 | 8 | 9 | 95.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.15476 | YES | 0.26335 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 95.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 1407-PM-121 B | PMCC-2 | ANTISCALANT DSING PUMP B | COOLING TOWER AREA | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.13691 | YES | 0.23299 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | - | PMCC-2 | ANTI SCALANT AGITATOR | COOLING TOWER AREA | A | MOTOR | 0.75 | kW | 3Ph | 400 | 0.75 | 0.853 | 1.6922 | 10.153 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 22 | 36.4 | 20 | 8 | 9 | 95.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.3137 | YES | 0.53383 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 95.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 1407-PM-119 A | PMCC-2 | COROSSION INHIBITOR DOSING PUMP -A | COOLING TOWER AREA | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.13691 | YES | 0.23299 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 1407-PM-119 B | PMCC-2 | COROSSION INHIBITOR DOSING PUMP -B | COOLING TOWER AREA | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 22 | 36.4 | 20 | 8 | 9 | 95.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.15476 | YES | 0.26335 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 95.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | - | PMCC-2 | COROSSION INHIBITOR AGITATOR | COOLING TOWER AREA | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.75 | 0.853 | 1.6922 | 10.153 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.27753 | YES | 0.47227 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 1407-PM-118 A | PMCC-2 | BIOCIDE DOSING PUMP -A | COOLING TOWER AREA | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 22 | 36.4 | 20 | 8 | 9 | 95.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.15476 | YES | 0.26335 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 95.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 1407-PM-118 B | PMCC-2 | BIOCIDE DOSING PUMP -B | COOLING TOWER AREA | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.13691 | YES | 0.23299 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | - | PMCC-2 | BIOCIDE AGITATOR | COOLING TOWER AREA | A | MOTOR | 0.75 | kW | 3Ph | 400 | 0.75 | 0.853 | 1.6922 | 10.153 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 22 | 36.4 | 20 | 8 | 9 | 95.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.3137 | YES | 0.53383 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 95.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 1407-PM-120 A | PMCC-2 | NaOCl DOSING PUMP -A | COOLING TOWER AREA | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.13691 | YES | 0.23299 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 1407-PM-120 B | PMCC-2 | NaOCl DOSING PUMP -B | COOLING TOWER AREA | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 22 | 36.4 | 20 | 8 | 9 | 95.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.15476 | YES | 0.26335 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 95.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | - | PMCC-2 | NaOCl AGITATOR | COOLING TOWER AREA | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.75 | 0.853 | 1.6922 | 10.153 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.27753 | YES | 0.47227 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 1407-PM-122 A | PMCC-2 | H2SO4 DOSING PUMP -A | COOLING TOWER AREA | A | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 22 | 36.4 | 20 | 8 | 9 | 95.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.15476 | YES | 0.26335 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 95.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 1407-PM-122 B | PMCC-2 | H2SO4 DOSING PUMP -B | COOLING TOWER AREA | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.13691 | YES | 0.23299 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | - | PMCC-2 | H2SO4 AGITATOR | COOLING TOWER AREA | B | MOTOR | 0.75 | kW | 3Ph | 400 | 0.75 | 0.853 | 1.6922 | 10.153 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.27753 | YES | 0.47227 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 | Q4Q5Q6 | 15 | 15 | [49 empty] | 1 | 1 | 1 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 1407-PM-117 A | PMCC-2 | DISPERSANT DOSING PUMP-A | COOLING TOWER AREA | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.13691 | YES | 0.23299 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 |  | 15 | 15
51 | 1407-PM-117 B | PMCC-2 | DISPERSANT DOSING PUMP-B | COOLING TOWER AREA | B | MOTOR | 0.37 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.8348 | 5.0088 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.13691 | YES | 0.23299 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | 84.4 |  | 2 |  | 15 | 15
|  |  | General Service Pumps Package | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-002A | PMCC-2 | SERVICE WATER PUMPS - A | NEAR FIRE WATER PUMP HOUSE | B | MOTOR | 2.2 | kW | 3Ph | 400 | 0.75 | 0.853 | 4.9637 | 29.7821 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.81408 | YES | 1.3853 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-002B | PMCC-2 | SERVICE WATER PUMPS - B | NEAR FIRE WATER PUMP HOUSE | A | MOTOR | 2.2 | kW | 3Ph | 400 | 0.75 | 0.853 | 4.9637 | 29.7821 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.81408 | YES | 1.3853 | YES | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4+PE Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001A | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - A | NEAR FIRE WATER PUMP HOUSE | B | MOTOR | 18.5 | kW | 3Ph | 400 | 0.75 | 0.853 | 41.7401 | 250.4406 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 2 | YES | 3.4228 | NO | 5.8247 | YES | 2R x 0.6/1kV x 3C x 4 Sqmm | 2R x 0.6/1kV x 3C x 4+PE Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001A | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - A-SPACE HEATER | NEAR FIRE WATER PUMP HOUSE | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001B | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - B | NEAR FIRE WATER PUMP HOUSE | A | MOTOR | 18.5 | kW | 3Ph | 400 | 0.75 | 0.853 | 41.7401 | 250.4406 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 2 | YES | 3.4228 | NO | 5.8247 | YES | 2R x 0.6/1kV x 3C x 4 Sqmm | 2R x 0.6/1kV x 3C x 4+PE Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001B | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - B-SPACE HEATER | NEAR FIRE WATER PUMP HOUSE | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001C | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - C | NEAR FIRE WATER PUMP HOUSE | B | MOTOR | 18.5 | kW | 3Ph | 400 | 0.75 | 0.853 | 41.7401 | 250.4406 | 0.2 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.35 | YES | 2.7439 | YES | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35+PE Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001C | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - C -SPACE HEATER | NEAR FIRE WATER PUMP HOUSE | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001D | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - D | NEAR FIRE WATER PUMP HOUSE | B | MOTOR | 18.5 | kW | 3Ph | 400 | 0.75 | 0.853 | 41.7401 | 250.4406 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4+PE | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 2 | YES | 3.4228 | NO | 5.8247 | YES | 2R x 0.6/1kV x 3C x 4 Sqmm | 2R x 0.6/1kV x 3C x 4+PE Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1409-PM-001D | PMCC-2 | CT MAKE UP WATER TRANSFER PUMPS - D-SPACE HEATER | NEAR FIRE WATER PUMP HOUSE | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 22 | 100 | 10 | 8 | 14 | 154 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.013 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | [55 empty] | 1 | 1 | 1 | 1 | 1 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | - | PMCC-2 | OUTGOING FEEDER FOR CT MAKE UP WATER TRANSFER PUMPS PANEL | NEAR FIRE WATER PUMP HOUSE | B | POWER | 74 | kW | 3Ph | 400 | 0.75 | 0.853 | 166.9604 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 150 | 3.5C X 150 | 3.5C X 150 | 0.6/1.0 | 293 | 0.264 | 0.0732 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 1.5036 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 1R x 0.6/1kV x 3.5C x 150 Sqmm | 84.4 |  | 2 |  | 48 | 48
53 | - | PMCC-2 | OUTGOING FEEDER FOR SERVICE WATER PUMPS PANEL | NEAR FIRE WATER PUMP HOUSE | B | POWER | 4.4 | kW | 3Ph | 400 | 0.75 | 0.853 | 9.9274 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 36.4 | 20 | 8 | 8 | 84.4 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.6282 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84.4 |  | 2 |  | 16 | 16
|  |  | Other Load | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 1420-MLDB-4-0002 | PMCC-2 | OUTGOING FEEDER FOR MLDB-2 / FEEDER | COOLING TOWER SUBSTATION | A | POWER | 63.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 113.9541 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 0.70685 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 37 |  | 2 |  | 39 | 39 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 1420-WDB-4-0002 | PMCC-2 | OUTGOING FEEDER FOR WDB-2 / FEEDER | COOLING TOWER SUBSTATION | A | POWER | 100 | kW | 3Ph | 400 | 0.85 | 0.95 | 178.7515 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 2 | YES | 0.74684 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 70 Sqmm | 2R x 0.6/1kV x 3.5C x 70 Sqmm | 74 |  | 4 |  | 36 | 72 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 1420-PDB-4-0002 | PMCC-2 | OUTGOING FEEDER FOR PDB-2 / FEEDER-1 | COOLING TOWER SUBSTATION | A | POWER | 301.1371 | kW | 3Ph | 400 | 0.85 | 0.95 | 538.2869 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 300 | 3.5C X 300 | 3.5C X 300 | 0.6/1.0 | 459 | 0.128 | 0.0711 | 20 | 0 | 5 | 8 | 4 | 37 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 0.63066 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 74 |  | 4 |  | 64 | 128 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 1420-PDB-4-0002 | PMCC-2 | OUTGOING FEEDER FOR PDB-2 / FEEDER-2 | COOLING TOWER SUBSTATION | B | POWER | 301.1371 | kW | 3Ph | 400 | 0.85 | 0.95 | 538.2869 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 300 | 3.5C X 300 | 3.5C X 300 | 0.6/1.0 | 459 | 0.128 | 0.0711 | 12 | 0 | 5 | 8 | 3 | 28 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 269.6166 | 2 | YES | 0.47726 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 2R x 0.6/1kV x 3.5C x 300 Sqmm | 56 |  | 4 |  | 64 | 128 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 1420-SWG-4-0002 | PMCC-2 | PMCC - 2 (INCOMER 1) | COOLING TOWER SUBSTATION | A | INCOMER | 3150 | kVA | 3Ph | 400 | 0.85544 | 0.91531 | 4967.4735 | LV BUSDUCT-400V | [110 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 1420-SWG-4-0002 | PMCC-2 | PMCC - 2 (INCOMER 2) | COOLING TOWER SUBSTATION | B | INCOMER | 3150 | kVA | 3Ph | 400 | 0.85544 | 0.91531 | 4967.4735 | LV BUSDUCT-400V | [110 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | PDB-2 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | HVAC SYSTEM | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 1420-ACDB-4-0201 | PDB-2 | COOLING TOWER SUBSTATION HVAC DB-201 | COOLING TOWER SUBSTATION | A | POWER | 15.79 | kW | 3Ph | 400 | 0.85 | 0.95 | 28.2249 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 22 | 0 | 10 | 8 | 4 | 44 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.8251 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 44 |  | 2 |  | 20 | 20 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 1420-ACDB-4-0202 | PDB-2 | WORKSHOP HVAC DB-202 | WORKSHOP | B | POWER | 43.37 | kW | 3Ph | 400 | 0.85 | 0.95 | 77.5245 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 17 | 95 | 10 | 8 | 13 | 143 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.8585 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 143 |  | 2 | Q3RR1R2R2.A | 39 | 39 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 1420-ACDB-4-0203 | PDB-2 | ADMIN BUILDING HVAC DB-203 | ADMIN BULDING-GROUND FLOOR | B | POWER | 11.97 | kW | 3Ph | 400 | 0.85 | 0.95 | 21.3965 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 17 | 133 | 10 | 8 | 17 | 185 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.6889 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 185 |  | 2 | Q3RR1R2SS.B | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | - | PDB-2 | ROOFTOP UNIT-1 | ADMIN BUILDING ROOF | A | MOTOR | 65 | kW | 3Ph | 400 | 0.85 | 0.954 | 115.7013 | 694.2077 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 2.5822 | YES | 7.3365 | YES | 1R x 0.6/1kV x 3C x 150 Sqmm | 1R x 0.6/1kV x 3C x 150+PE Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 39 | 39 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 0 | 0 | 39 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | - | PDB-2 | ROOFTOP UNIT-1-SPACE HEATER | ADMIN BUILDING ROOF | A | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.2892 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | 0 | 0 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | - | PDB-2 | HEATER-1 | ADMIN BUILDING ROOF | A | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.2422 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | - | PDB-2 | HUMIDIFIER-1 | ADMIN BUILDING ROOF | A | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0511 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | - | PDB-2 | ROOFTOP UNIT-2 | ADMIN BUILDING ROOF | B | MOTOR | 65 | kW | 3Ph | 400 | 0.85 | 0.954 | 115.7013 | 694.2077 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 2.5822 | YES | 7.3365 | YES | 1R x 0.6/1kV x 3C x 150 Sqmm | 1R x 0.6/1kV x 3C x 150+PE Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 39 | 39 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 0 | 0 | 39 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | - | PDB-2 | ROOFTOP UNIT-2-SPACE HEATER | ADMIN BUILDING ROOF | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.2892 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | 0 | 0 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | - | PDB-2 | HEATER-2 | ADMIN BUILDING ROOF | B | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.2422 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | - | PDB-2 | HUMIDIFIER-2 | ADMIN BUILDING ROOF | B | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0511 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | - | PDB-2 | ROOFTOP UNIT-3 | ADMIN BUILDING ROOF | B | MOTOR | 65 | kW | 3Ph | 400 | 0.85 | 0.95 | 116.1884 | 697.1307 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 150 | 3C X 150 | 3C X 150+PE | 0.6/1.0 | 293 | 0.264 | 0.0732 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 172.1082 | 1 | YES | 2.593 | YES | 7.3674 | YES | 1R x 0.6/1kV x 3C x 150 Sqmm | 1R x 0.6/1kV x 3C x 150+PE Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 39 | 39 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 0 | 0 | 39 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | - | PDB-2 | ROOFTOP UNIT-3-SPACE HEATER | ADMIN BUILDING ROOF | B | POWER | 0.2 | kW | 1Ph | 230 | 0.85 | 0.95 | 1.0769 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 2.5 | 3C X 2.5 | 3C X 2.5 | 0.6/1.0 | 28 | 9.48 | 0.1007 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 16.4472 | 1 | YES | 1.2892 | YES | NA | NA | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 1R x 0.6/1kV x 3C x 2.5 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 14 | 14 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 14 | 0 | 0 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | - | PDB-2 | HEATER-3 | ADMIN BUILDING ROOF | B | POWER | 15 | kW | 3Ph | 400 | 0.85 | 0.95 | 26.8127 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 2.2422 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | - | PDB-2 | HUMIDIFIER-3 | ADMIN BUILDING ROOF | B | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95 | 17.8751 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 17 | 143 | 10 | 8 | 18 | 196 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 2.0511 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 196 |  | 2 | Q3RR1R2SS.B | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 1420-ACDB-4-0204 | PDB-2 | FIRE STATION BUILDING HVAC DB -204 | FIRE STATION BUILDING | A | POWER | 48.79 | kW | 3Ph | 400 | 0.85 | 0.95 | 87.2128 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 120 | 3.5C X 120 | 3.5C X 120 | 0.6/1.0 | 257 | 0.324 | 0.0726 | 17 | 144 | 10 | 8 | 18 | 197 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 150.9618 | 1 | YES | 2.3334 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 1R x 0.6/1kV x 3.5C x 120 Sqmm | 197 |  | 2 | Q3RR1R2SS1S1.A | 43 | 43 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 43 | 43 | 43 | 0 | 0 | 43 | 0 | 0 | 43 | 43 | 0 | 0 | 0 | 0 | 0
72 | 1420-ACDB-4-0205 | PDB-2 | STORES HVAC DB -205 | STORES | B | POWER | 25.92 | kW | 3Ph | 400 | 0.85 | 0.95 | 46.3324 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 17 | 187 | 10 | 8 | 23 | 245 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 1.903 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 245 |  | 2 | Q3RR1R2SS1TTA | 39 | 39 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 |  | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 0 | 0 | 39 | 0 | 0 | 39 | 0 | 39 | 0 | 39 | 0 | 0
73 | 1420-ACDB-4-0206 | PDB-2 | CANTEEN BUILDING HVAC DB-206 | CANTEEN BUILDING | A | POWER | 28.99 | kW | 3Ph | 400 | 0.85 | 0.95 | 51.82 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 95 | 3.5C X 95 | 3.5C X 95 | 0.6/1.0 | 221 | 0.41 | 0.0734 | 17 | 181 | 10 | 8 | 22 | 238 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 129.8154 | 1 | YES | 2.0676 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 1R x 0.6/1kV x 3.5C x 95 Sqmm | 238 |  | 2 | Q3RR1R2SS.A | 39 | 39 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 39 | 0 | 0 | 39 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 1420-ACDB-4-0207 | PDB-2 | OCCUPATIONAL HEALTH CENTER HVAC DB -207 | OCCUPATIONAL HEALTH CENTER / DISPENSARY | A | POWER | 16.04 | kW | 3Ph | 400 | 0.85 | 0.95 | 28.6717 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 17 | 201 | 10 | 8 | 24 | 260 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 1 | YES | 2.3846 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 1R x 0.6/1kV x 3.5C x 50 Sqmm | 260 |  | 2 | Q3RR1R2SS1TT1T1.A | 30 | 30 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 30 | 30 | 0 | 30 | 0
|  |  | Other Load | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 1420-SWG-4-0002 | PDB-2 | AUX POWER SUPPLY - PMCC-2 (BUS-A) | COOLING TOWER SUBSTATION | A | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 17 | 3 | 5 | 8 | 4 | 37 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.72526 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 37 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 1420-SWG-4-0002 | PDB-2 | AUX POWER SUPPLY - PMCC-2 (BUS-B) | COOLING TOWER SUBSTATION | B | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 17 | 3 | 5 | 8 | 4 | 37 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.72526 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 37 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 1420-SWG-4-0002 | PDB-2 | AUX POWER SUPPLY NSPBD SYSTEM-2A | COOLING TOWER SUBSTATION | A | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 17 | 5 | 5 | 8 | 4 | 39 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.76446 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 39 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 1420-SWG-4-0002 | PDB-2 | AUX POWER SUPPLY NSPBD SYSTEM-2B | COOLING TOWER SUBSTATION | B | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 17 | 5 | 5 | 8 | 4 | 39 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.76446 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 39 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 1420-TFD-2-0003 | PDB-2 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-3 | COOLING TOWER SUBSTATION | A | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 17 | 8 | 5 | 8 | 4 | 42 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.49396 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 42 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 1420-TFD-2-0004 | PDB-2 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-4 | COOLING TOWER SUBSTATION | B | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 17 | 8 | 5 | 8 | 4 | 42 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.49396 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 42 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | - | PDB-2 | CRANE - Workshop building- Single Girder EOT Crane - (20T) | WORKSHOP BUILDING | A | POWER | 25 | kW | 3Ph | 400 | 0.75 | 0.853 | 56.4055 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 70 | 3.5C X 70 | 3.5C X 70 | 0.6/1.0 | 177 | 0.567 | 0.0752 | 22 | 95 | 20 | 8 | 15 | 160 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 103.9698 | 1 | YES | 1.8562 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 1R x 0.6/1kV x 3.5C x 70 Sqmm | 160 |  | 2 | Q3RR1R2R2.A | 36 | 36 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | 36 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | - | PDB-2 | Electric Hoist - Fire water pump house) - Electric Hoist (3T) | Fire water pump house | A | MOTOR | 5 | kW | 3Ph | 400 | 0.75 | 0.853 | 11.2811 | 67.6867 | 0.2 | 65 | 0 | 0 | TRENCH | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 22 | 105 | 20 | 8 | 16 | 171 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.5182 | YES | 4.3923 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 171 |  | 2 | E0Q1Q4Q5U | 16 | 16 | [10 empty] | 1 | [35 empty] | 1 |  |  | 1 | 1 | [17 empty] | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16
80 | 1420-PDB-4-0002 | PMCC-2 | PDB-2 (INCOMER 1) | COOLING TOWER SUBSTATION | A | INCOMER | 348.6206 | kW | 3Ph | 400 | 0.85 | 0.95042 | 622.8884 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 1420-PDB-4-0002 | PMCC-2 | PDB-2 (INCOMER 2) | COOLING TOWER SUBSTATION | B | INCOMER | 348.6206 | kW | 3Ph | 400 | 0.85 | 0.95042 | 622.8884 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MLDB-2 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | NLP-101 | MLDB-02 | LIGHTING DB-101 | WORKSHOP & MAINTENANCE BULDING (GROUND FLOOR) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 95 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.7845 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 150 |  | 2 | Q3RR1R2R2.A | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | NLP-102 | MLDB-02 | LIGHTING DB-102 | WORKSHOP&MAINTENANCE BULDING (FIRST FLOOR) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 100 | 10 | 8 | 15 | 156 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.81588 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 156 |  | 2 | Q3RR1R2R2.A | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | NLP-103 | MLDB-02 | LIGHTING DB-103 | ADMIN BULDING-GROUND FLOOR |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 133 | 10 | 8 | 18 | 192 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.0042 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 192 |  | 2 | Q3RR1R2SS.B | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | NLP-104 | MLDB-02 | LIGHTING DB-104 | ADMIN BULDING-FIRST FLOOR |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 143 | 10 | 8 | 19 | 203 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.0617 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 203 |  | 2 | Q3RR1R2SS.B | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | NLP-105 | MLDB-02 | LIGHTING DB-105 | COOLING TOWER PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 95 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.7845 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 150 |  | 2 | Q3RR1R1.A | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | NLP-106 | MLDB-02 | LIGHTING DB-106 | CANTEEN BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 181 | 10 | 8 | 23 | 245 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.2813 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 245 |  | 2 | Q3RR1R2SS.A | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | NLP-107 | MLDB-02 | LIGHTING DB-107 | FIRE STATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 144 | 10 | 8 | 19 | 204 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.0669 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 204 |  | 2 | Q3RR1R2SS1S1.A | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 0
89 | NLP-108 | MLDB-02 | LIGHTING DB-108 | STORE |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 187 | 10 | 8 | 23 | 251 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.3127 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 251 |  | 2 | Q3RR1R2SS1TTA | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 |  | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 25 | 0 | 25 | 0 | 0
90 | NLP-109 | MLDB-02 | LIGHTING DB-109 | OCCUPATIONAL HEALTH CENTER / DISPENSARY |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 201 | 10 | 8 | 25 | 267 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.3964 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 267 |  | 2 | Q3RR1R2SS1TT1T1.A | 25 | 25 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 25 | 25 | 0 | 25 | 0
91 | NLP-110 | MLDB-02 | LIGHTING DB-110 | COOLING TOWER SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 23 | 0 | 10 | 8 | 5 | 46 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.24058 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 46 |  | 2 |  | 25 | 25 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | NLP-111 | MLDB-02 | STREET LIGHTING DB- 02 | ROAD AND EXTERNAL AREA (INCLUDING COOLING WATER PUMP & FIRE WATER PUMP AREA) |  | POWER | 20 | kW | 3Ph | 400 | 0.85 | 0.95042 | 35.7345 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 23 | 20 | 10 | 8 | 7 | 68 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2274 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 68 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | NLP-112 | MLDB-02 / NLP-107 | LIGHTING & POWER DB-113 | SECURITY ROOM-1 |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 0 | 10 | 8 | 6 | 58 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.47497 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 58 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | NLP-113 | MLDB-02 / NLP-107 | LIGHTING & POWER DB-114 | SECURITY ROOM-3 |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 34 | 0 | 10 | 8 | 6 | 58 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.47497 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 58 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | HM-101 | MLDB-02 | HIGH MAST-101 | NEAR WAREHOUSE AREA |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 23 | 225 | 10 | 8 | 27 | 293 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3994 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 293 |  | 2 | Q3RR1R2SS1TT1 | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0
96 | HM-102 | MLDB-02 | HIGH MAST-102 | NEAR WAREHOUSE AREA |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 23 | 225 | 10 | 8 | 27 | 293 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3994 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 293 |  | 2 | Q3RR1R2SS1TT1 | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 | 1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 0 | 0
97 | HM-103 | MLDB-02 | HIGH MAST-103 | NEAR WORKSHOP & MAINTENACE AREA |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 23 | 95 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.2284 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 150 |  | 2 | Q3R | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 1420-MLDB-4-0002 | PMCC-2 | MAIN LIGHTING DB-002 (INCOMER) | COOLING TOWER SUBSTATION |  | INCOMER | 85 | kW | 3Ph | 400 | 0.85 | 0.95042 | 200 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EMLDB-2 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | ELP-101 | EMLDB-2 | EMERGENCY LIGHTING DB-101 | WORKSHOP & MAINTENANCE BULDING (GROUND FLOOR) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 21 | 95 | 10 | 8 | 14 | 148 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.9431 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 148 |  | 2 | Q3RR1R2R2.A | 20 | 20 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | ELP-102 | EMLDB-2 | EMERGENCY LIGHTING DB-102 | WORKSHOP&MAINTENANCE BULDING (FIRST FLOOR) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 21 | 100 | 10 | 8 | 14 | 153 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 2.0087 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 153 |  | 2 | Q3RR1R2R2.A | 20 | 20 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | ELP-103 | EMLDB-2 | EMERGENCY LIGHTING DB-103 | ADMIN BULDING-GROUND FLOOR |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 21 | 133 | 10 | 8 | 18 | 190 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 2.4945 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 190 |  | 2 | Q3RR1R2SS.B | 20 | 20 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 20 | 0 | 0 | 20 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | ELP-104 | EMLDB-2 | EMERGENCY LIGHTING DB-104 | ADMIN BULDING-FIRST FLOOR |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 21 | 143 | 10 | 8 | 19 | 201 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.646 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 201 |  | 2 | Q3RR1R2SS.B | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | ELP-105 | EMLDB-02 | EMERGENCY LIGHTING DB-105 | COOLING TOWER PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 23 | 95 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.9693 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 150 |  | 2 | Q3RR1R1.A | 20 | 20 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | ELP-106 | EMLDB-2 | EMERGENCY LIGHTING DB-106 | CANTEEN BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 21 | 181 | 10 | 8 | 22 | 242 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.9818 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 242 |  | 2 | Q3RR1R2SS.A | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | ELP-107 | EMLDB-2 | EMERGENCY LIGHTING DB-107 | FIRE STATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 21 | 144 | 10 | 8 | 19 | 202 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6542 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 202 |  | 2 | Q3RR1R2SS1S1.A | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0
106 | ELP-108 | EMLDB-2 | EMERGENCY LIGHTING DB-108 | STORE |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 21 | 187 | 10 | 8 | 23 | 249 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.0391 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 249 |  | 2 | Q3RR1R2SS1TTA | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 |  | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 21 | 0 | 21 | 0 | 0
107 | ELP-109 | EMLDB-2 | EMERGENCY LIGHTING DB-109 | OCCUPATIONAL HEALTH CENTER / DISPENSARY |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 21 | 201 | 10 | 8 | 24 | 264 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.1619 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 264 |  | 2 | Q3RR1R2SS1TT1T1.A | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 21 | 21 | 0 | 21 | 0
108 | ELP-110 | EMLDB-2 | EMERGENCY LIGHTING DB-110 | COOLING TOWER SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 23 | 9 | 10 | 8 | 5 | 55 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0.72208 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 55 |  | 2 |  | 20 | 20 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 1420-EMLDB-4-0002 | EPMCC-1 | EMERGENCY MAIN LIGHTING DB-002 (INCOMER) | COOLING TOWER SUBSTATION |  | INCOMER | 20 | kW | 3Ph | 400 | 0.85 | 0.95042 | 63 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WDB-2 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | WSDB-101 | WDB-02 | POWER RECEPTACLE DB-101 | WORKSHOP & MAINTENANCE BULDING (GROUND FLOOR) |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.95042 | 17.8672 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 95 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.1435 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 150 |  | 2 | Q3RR1R2R2.A | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | WSDB-102 | WDB-02 | POWER RECEPTACLE DB-102 | WORKSHOP&MAINTENANCE BULDING (FIRST FLOOR) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 100 | 10 | 8 | 15 | 156 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.59461 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 156 |  | 2 | Q3RR1R2R2.A | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | WSDB-103 | WDB-02 | POWER RECEPTACLE DB-103 | ADMIN BULDING-GROUND FLOOR |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 133 | 10 | 8 | 18 | 192 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.73183 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 192 |  | 2 | Q3RR1R2SS.B | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | WSDB-104 | WDB-02 | POWER RECEPTACLE DB-104 | ADMIN BULDING-FIRST FLOOR |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 143 | 10 | 8 | 19 | 203 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.77376 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 203 |  | 2 | Q3RR1R2SS.B | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  | 1 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | WSDB-105 | WDB-02 | POWER RECEPTACLE DB-105 | COOLING TOWER PACKAGE (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 95 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.57174 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 150 |  | 2 | Q3RR1R1.A | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 |  | 1 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | WSDB-106 | WDB-02 | POWER RECEPTACLE DB-106 | CANTEEN BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 181 | 10 | 8 | 23 | 245 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.93384 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 245 |  | 2 | Q3RR1R2SS.A | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 | 1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | WSDB-107 | WDB-02 | POWER RECEPTACLE DB-107 | FIRE STATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 144 | 10 | 8 | 19 | 204 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.77757 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 204 |  | 2 | Q3RR1R2SS1S1.A | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0
117 | WSDB-108 | WDB-02 | POWER RECEPTACLE DB-108 | STORE |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 187 | 10 | 8 | 23 | 251 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.95671 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 251 |  | 2 | Q3RR1R2SS1TTA | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 |  | 1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 27 | 0 | 27 | 0 | 0
118 | WSDB-109 | WDB-02 | POWER RECEPTACLE DB-109 | OCCUPATIONAL HEALTH CENTER / DISPENSARY |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 201 | 10 | 8 | 25 | 267 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.0177 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 267 |  | 2 | Q3RR1R2SS1TT1T1.A | 27 | 27 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 27 | 27 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 27 | 27 | 0 | 27 | 0
119 | WSDB-110 | WDB-02 | POWER RECEPTACLE DB-110 | COOLING TOWER SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 23 | 9 | 10 | 8 | 5 | 55 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.20964 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 55 |  | 2 |  | 27 | 27 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | WS-101 & 102 | WDB-02 | WELDING SOCKET -101 & 102 | COOLING TOWER SUBSTATION & PACKAGE |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 23 | 9 | 10 | 8 | 5 | 55 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.4504 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 55 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | WS-103 & 104 | WDB-02 | WELDING SOCKET -103 & 104 | FIRE STATION BUILDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 23 | 144 | 10 | 8 | 19 | 204 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6706 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 204 |  | 2 | Q3RR1R2SS1S1.A | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  |  | 1 |  |  | 1 | 1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 | 21 | 0 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0
122 | WS-105 & 106 | WDB-02 | WELDING SOCKET -105 & 106 | WORKSHOP & MAINTENANCE BULDING |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 8.9336 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 23 | 95 | 10 | 8 | 14 | 150 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.2284 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 150 |  | 2 | Q3RR1R2R2.A | 21 | 21 | [48 empty] | 1 | [5 empty] | 1 | 1 | 1 |  | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 1420-WDB-4-0002 | PMCC-2 | WELDING & RECEPTACLE DB-002 (INCOMER) |  |  | INCOMER | 42.5 | kW | 3Ph | 400 | 0.85 | 0.95042 | 125 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | COOLING TOWER SUBSTATION HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | COOLING TOWER SUBSTATION HVAC DB | CONTROL ROOM-SPLIT AC-1 | COOLING TOWER SUBSTATION |  | POWER | 3 | kW | 1Ph | 230 | 0.85 | 0.95 | 16.1529 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 10 | 0 | 10 | 5 | 3 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | COOLING TOWER SUBSTATION HVAC DB | CONTROL ROOM-SPLIT AC-2 | COOLING TOWER SUBSTATION |  | POWER | 3 | kW | 1Ph | 230 | 0.85 | 0.95 | 16.1529 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 10 | 0 | 10 | 5 | 3 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X | - | COOLING TOWER SUBSTATION HVAC DB | CONTROL ROOM-SPLIT AC-3 | COOLING TOWER SUBSTATION |  | POWER | 3 | kW | 1Ph | 230 | 0.85 | 0.95 | 16.1529 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 10 | 0 | 10 | 5 | 3 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
124 | - | COOLING TOWER SUBSTATION HVAC DB | LV SWGR VENTILATION FAN 1 | COOLING TOWER SUBSTATION |  | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 10 | 0 | 10 | 5 | 3 | 28 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.82326 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 28 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | - | COOLING TOWER SUBSTATION HVAC DB | LV SWGR VENTILATION FAN 2 | COOLING TOWER SUBSTATION |  | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 10 | 0 | 10 | 5 | 3 | 28 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.82326 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 28 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | COOLING TOWER SUBSTATION HVAC DB | LV SWGR VENTILATION FAN 3 | COOLING TOWER SUBSTATION |  | POWER | 1.1 | kW | 1Ph | 230 | 0.85 | 0.95 | 5.9227 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 10 | 0 | 10 | 5 | 3 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
126 | 1420-ACDB-4-0201 | PDB-2 | COOLING TOWER SUBSTATION HVAC DB-201 INCOMER | COOLING TOWER SUBSTATION |  | INCOMER | 11.2632 | kVA | 3Ph | 400 | 0.85 | 0.95 | 17.1131 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WORKSHOP HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 |  | WORKSHOP HVAC DB | WORKSHOP FAN 1-VENTILATION FAN | WORKSHOP |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.80596 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 |  | WORKSHOP HVAC DB | WORKSHOP FAN 2-VENTILATION FAN | WORKSHOP |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.80596 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 |  | WORKSHOP HVAC DB | WORKSHOP FAN 3-VENTILATION FAN | WORKSHOP |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.80596 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 |  | WORKSHOP HVAC DB | WORKSHOP FAN 4-VENTILATION FAN | WORKSHOP |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.80596 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 |  | WORKSHOP HVAC DB | WORKSHOP FAN 5-VENTILATION FAN | WORKSHOP |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.80596 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  | WORKSHOP HVAC DB | WORKSHOP FAN 6-VENTILATION FAN | WORKSHOP |  | POWER |  | kW | 3Ph | 400 | 0.95 | 0.85 | 0 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 0 | YES | #DIV/0! | #DIV/0! | NA | NA | 0R x 0.6/1kV x 4C x 4 Sqmm | 0R x 0.6/1kV x 4C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
132 |  | WORKSHOP HVAC DB | GF - TOILET - VENTILATION FAN | WORKSHOP |  | POWER | 0.25 | kW | 3Ph | 230 | 0.95 | 0.85 | 0.77718 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.27701 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  | WORKSHOP HVAC DB | ELECTRICAL ROOM - VENTILATION FAN 1 | WORKSHOP |  | POWER |  | kW | 1Ph | 230 | 0.95 | 0.85 | 0 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 0 | YES | #DIV/0! | #DIV/0! | NA | NA | 0R x 0.6/1kV x 3C x 4 Sqmm | 0R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X |  | WORKSHOP HVAC DB | ELECTRICAL ROOM - VENTILATION FAN 2 (S/B) | WORKSHOP |  | POWER |  | kW | 1Ph | 230 | 0.95 | 0.85 | 0 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 0 | YES | #DIV/0! | #DIV/0! | NA | NA | 0R x 0.6/1kV x 3C x 4 Sqmm | 0R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
133 |  | WORKSHOP HVAC DB | SPARE PARTS ROOM - VENTILATION FAN | WORKSHOP |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.47978 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 84 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 |  | WORKSHOP HVAC DB | WELDING ROOM - VENTILATION FAN | WORKSHOP |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.47978 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 84 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 |  | WORKSHOP HVAC DB | 1F - LADIES & GENTS TOILET | WORKSHOP |  | POWER | 0.25 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.44688 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.091586 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 84 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 |  | WORKSHOP HVAC DB | 1F - PANTRY AND MESS ROOM | WORKSHOP |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 61 | 0 | 10 | 5 | 8 | 84 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.47978 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 84 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 |  | WORKSHOP HVAC DB | ELECTRICAL WORKSHOP - SPLIT AC 1 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 |  | WORKSHOP HVAC DB | I & C WORKSHOP - SPLIT AC | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 |  | WORKSHOP HVAC DB | TECHNICIAN ROOM - SPLIT AC 1 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 |  | WORKSHOP HVAC DB | TECHNICIAN ROOM - SPLIT AC 2 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 |  | WORKSHOP HVAC DB | 1F - TESTING ROOM & LABORATORY - SPLIT AC 1 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 |  | WORKSHOP HVAC DB | 1F - TRAINING ROOM - SPLIT AC 1 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 |  | WORKSHOP HVAC DB | 1F - TRAINING ROOM - SPLIT AC 2 | WORKSHOP |  | POWER | 1.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.5826 | YES | NA | NA | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6 Sqmm | 69 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 |  | WORKSHOP HVAC DB | 1F - OFFICE ROOM - SPLIT AC 1 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 |  | WORKSHOP HVAC DB | 1F - OFFICE ROOM - SPLIT AC 2 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 |  | WORKSHOP HVAC DB | 1F - MEETING ROOM - SPLIT AC 1 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 |  | WORKSHOP HVAC DB | 1F - MEETING ROOM - SPLIT AC 2 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 |  | WORKSHOP HVAC DB | 1F - MEETING ROOM - SPLIT AC 3 | WORKSHOP |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 |  | WORKSHOP HVAC DB | ELECTRICAL WORKSHOP - SPLIT AC 2 | ADMIN BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 |  | WORKSHOP HVAC DB | 1F - TESTING ROOM & LABORATORY - SPLIT AC 2 | ADMIN BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 47 | 0 | 10 | 5 | 7 | 69 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.2947 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 69 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 1420-ACDB-4-0202 | PDB-2 | WORKSHOP HVAC DB-202 INCOMER | WORKSHOP |  | INCOMER | 54.6737 | kW | 3Ph | 400 | 0.95 | 0.85 | 97.73 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADMIN BUILDING HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 |  | ADMIN BUILDING HVAC DB | CMD CABIN - SPLIT AC | ADMIN BUILDING |  | POWER | 1.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 2.6813 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.34018 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 |  | ADMIN BUILDING HVAC DB | LADIES PRAYER ROOM - SPLIT AC | ADMIN BUILDING |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.79375 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 |  | ADMIN BUILDING HVAC DB | MEN'S PRAYER ROOM-1 | ADMIN BUILDING |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.79375 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 |  | ADMIN BUILDING HVAC DB | MEN'S PRAYER ROOM-2 | ADMIN BUILDING |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.79375 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 |  | ADMIN BUILDING HVAC DB | CMD TOILET - VENTILATION | ADMIN BUILDING |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.29701 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 52 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 |  | ADMIN BUILDING HVAC DB | ELECTRICAL ROOM - VENTILATION FAN 1 | ADMIN BUILDING |  | POWER | 0.55 | kW | 1Ph | 230 | 0.95 | 0.85 | 2.9614 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.65342 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 52 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 |  | ADMIN BUILDING HVAC DB | ELECTRICAL ROOM - VENTILATION FAN 2 | ADMIN BUILDING |  | POWER | 0.55 | kW | 1Ph | 230 | 0.95 | 0.85 | 2.9614 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.65342 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 52 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 |  | ADMIN BUILDING HVAC DB | GF-MAIN TOILET - VENTILATION FAN | ADMIN BUILDING |  | POWER | 0.37 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.66138 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.08391 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 |  | ADMIN BUILDING HVAC DB | 1F-MAIN TOILET - VENTILATION FAN | ADMIN BUILDING |  | POWER | 0.25 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.44688 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.056696 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 |  | ADMIN BUILDING HVAC DB | 1F - RECORD ROOM - VENTILATION FAN | ADMIN BUILDING |  | POWER | 0.37 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.66138 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.08391 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 |  | ADMIN BUILDING HVAC DB | 1F - PANTRY - VENTILATION FAN | ADMIN BUILDING |  | POWER | 0.37 | kW | 3ph | 400 | 0.95 | 0.85 | 0.66138 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.08391 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 52 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 |  | ADMIN BUILDING HVAC DB | 1F - FINANCE & ACCOUNT STORE - VENTILATION FAN | ADMIN BUILDING |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.29701 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 52 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 |  | ADMIN BUILDING HVAC DB | 1F - PROCUREMENT STORE - VENTILATION FAN 1 | ADMIN BUILDING |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.29701 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 52 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 |  | ADMIN BUILDING HVAC DB | 1F - PROCUREMENT STORE - VENTILATION FAN 2 (S/B) | ADMIN BUILDING |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.29701 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 52 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 |  | ADMIN BUILDING HVAC DB | GF - PANTRY - VENTILATION FAN | ADMIN BUILDING |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 32 | 0 | 10 | 5 | 5 | 52 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.29701 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 52 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 1420-ACDB-4-0203 | PDB-2 | ADMIN BUILDING HVAC DB-203 INCOMER | ADMIN BULDING-GROUND FLOOR |  | INCOMER | 11.9926 | kW | 3Ph | 400 | 0.95 | 0.85 | 21.437 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | FIRE STATION BUILDING HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 |  | FIRE STATION BUILDING HVAC DB | SAFETY TRAINING ROOM - SPLIT AC 1 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 |  | FIRE STATION BUILDING HVAC DB | SAFETY TRAINING ROOM - SPLIT AC 2 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 |  | FIRE STATION BUILDING HVAC DB | SAFETY TRAINING ROOM - SPLIT AC 3 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 |  | FIRE STATION BUILDING HVAC DB | CFO CABIN - SPLIT AC | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 |  | FIRE STATION BUILDING HVAC DB | FIRE PERSONNEL ROOM - SPLIT AC 1 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 |  | FIRE STATION BUILDING HVAC DB | FIRE PERSONNEL ROOM - SPLIT AC 2 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 |  | FIRE STATION BUILDING HVAC DB | FIRE PERSONNEL ROOM - SPLIT AC 3 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 |  | FIRE STATION BUILDING HVAC DB | FITNESS AREA - SPLIT AC 1 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 |  | FIRE STATION BUILDING HVAC DB | FITNESS AREA - SPLIT AC 2 | FIRE STATION BUILDING |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.7626 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 53 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 |  | FIRE STATION BUILDING HVAC DB | TOILET 1 - VENTILATION FAN | FIRE STATION BUILDING |  | POWER | 0.25 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.44688 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.057787 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 53 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 |  | FIRE STATION BUILDING HVAC DB | TOILET 2 - VENTILATION FAN | FIRE STATION BUILDING |  | POWER | 0.25 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.44688 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.057787 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 53 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 |  | FIRE STATION BUILDING HVAC DB | RECORD ROOM - VENTILATION FAN | FIRE STATION BUILDING |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.30272 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 53 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 |  | FIRE STATION BUILDING HVAC DB | SECURITY ROOM - TYPE 1 - SPLIT AC 1 | SECURITY ROOM |  | POWER | 1.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8163 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 53 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 |  | FIRE STATION BUILDING HVAC DB | SECURITY ROOM - TYPE 1 - SPLIT AC 2 | SECURITY ROOM |  | POWER | 1.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8163 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 53 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 |  | FIRE STATION BUILDING HVAC DB | SECURITY ROOM - TYPE 2 | SECURITY ROOM |  | POWER | 1.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.8163 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 53 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 |  | FIRE STATION BUILDING HVAC DB | TOILET - VENTILATION FAN | SECURITY ROOM |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.30272 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 53 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 |  | FIRE STATION BUILDING HVAC DB | CHANGE ROOM - VENTILATION FAN | SECURITY ROOM |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 33 | 0 | 10 | 5 | 5 | 53 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.30272 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 53 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 1420-ACDB-4-0204 | PDB-2 | FIRE STATION BUILDING HVAC DB -204 INCOMER | FIRE STATION BUILDING |  | INCOMER | 23.2842 | kW | 3Ph | 400 | 0.95 | 0.85 | 41.6209 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | STORES HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 |  | STORES HVAC DB | OFFICE-SPLIT AC-1 | STORES |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 31 | 0 | 10 | 5 | 5 | 51 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6961 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 51 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 |  | STORES HVAC DB | OFFICE-SPLIT AC-2 | STORES |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 31 | 0 | 10 | 5 | 5 | 51 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6961 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 51 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 |  | STORES HVAC DB | OFFICE-SPLIT AC-3 | STORES |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 31 | 0 | 10 | 5 | 5 | 51 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6961 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 51 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  | STORES HVAC DB | OFFICE-SPLIT AC-4 | STORES |  | POWER |  | kW | 1Ph | 230 | 0.95 | 0.85 | 0 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 31 | 0 | 10 | 5 | 5 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 0 | YES | #DIV/0! | #DIV/0! | NA | NA | 0R x 0.6/1kV x 3C x 6 Sqmm | 0R x 0.6/1kV x 3C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
189 |  | STORES HVAC DB | STORE MANAGER ROOM-SPLIT AC | STORES |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.4278 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 73 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 1 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 2 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 3 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 4 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 5 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 6 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 7 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 8 | STORES |  | POWER | 2.2 | kW | 3Ph | 400 | 0.95 | 0.85 | 3.9325 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 | 73 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.70042 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 73 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  | STORES HVAC DB | VENTILATION FAN (ROOF EXTRACTOR) 9 | STORES |  | POWER |  | kW | 1Ph | 230 | 0.95 | 0.85 | 0 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 51 | 0 | 10 | 5 | 7 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 0 | YES | #DIV/0! | #DIV/0! | NA | NA | 0R x 0.6/1kV x 3C x 4 Sqmm | 0R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
198 |  | STORES HVAC DB | TOILET - VENTILATION FAN | STORES |  | POWER | 0.25 | kW | 3Ph | 400 | 0.75 | 0.853 | 0.56406 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 83 | 20 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.14907 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 136 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 |  | STORES HVAC DB | CHEMICAL STORAGE | STORES |  | POWER | 0.55 | kW | 3Ph | 400 | 0.75 | 0.853 | 1.2409 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 83 | 20 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.32795 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 136 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 1420-ACDB-4-0205 | PDB-2 | STORES HVAC DB -205 INCOMER | STORES |  | INCOMER | 18.8421 | kW | 3Ph | 400 | 0.95 | 0.85 | 33.6805 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | CANTEEN BUILDING HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 |  | CANTEEN BUILDING HVAC DB | 36 PERSON DINING UNIT 1-SPLIT AC |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 |  | CANTEEN BUILDING HVAC DB | 36 PERSON DINING UNIT 2-SPLIT AC |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 |  | CANTEEN BUILDING HVAC DB | 36 PERSON DINING UNIT 3-SPLIT AC |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 |  | CANTEEN BUILDING HVAC DB | 36 PERSON DINING UNIT 4-SPLIT AC |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 |  | CANTEEN BUILDING HVAC DB | 24 PERSON DINING UNIT 1-SPLIT AC |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 |  | CANTEEN BUILDING HVAC DB | 24 PERSON DINING UNIT 2-SPLIT AC |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 |  | CANTEEN BUILDING HVAC DB | 24 PERSON DINING UNIT 3-SPLIT AC |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  | CANTEEN BUILDING HVAC DB | SERVING COUNTER UNIT 1-SPLIT AC |  |  | POWER |  | kW | 1Ph | 230 | 0.95 | 0.85 | 0 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 30 | 0 | 10 | 5 | 5 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 |  | YES | #DIV/0! | #DIV/0! | NA | NA | R x 0.6/1kV x 3C x 6 Sqmm | R x 0.6/1kV x 3C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
X |  | CANTEEN BUILDING HVAC DB | SERVING COUNTER UNIT 2-SPLIT AC |  |  | POWER |  | kW | 1Ph | 230 | 0.95 | 0.85 | 0 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 30 | 0 | 10 | 5 | 5 |  | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 |  | YES | #DIV/0! | #DIV/0! | NA | NA | R x 0.6/1kV x 3C x 6 Sqmm | R x 0.6/1kV x 3C x 6 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
208 |  | CANTEEN BUILDING HVAC DB | STAFF--SPLIT AC-1 |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 |  | CANTEEN BUILDING HVAC DB | STAFF--SPLIT AC-2 |  |  | POWER | 3.5 | kW | 1Ph | 230 | 0.95 | 0.85 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 1.6629 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 50 |  | 2 |  | 19 | 19 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 |  | CANTEEN BUILDING HVAC DB | LADIES TOILET -VENTILATION FAN |  |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.28558 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 50 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 |  | CANTEEN BUILDING HVAC DB | GENTS TOILET-VENTILATION FAN |  |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.28558 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 50 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 |  | CANTEEN BUILDING HVAC DB | STAFF TOILET-VENTILATION FAN |  |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.28558 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 50 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 |  | CANTEEN BUILDING HVAC DB | WEIGHING AREA-VENTILATION FAN | CANTEEN BUILDING |  | POWER | 0.25 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.44688 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.054516 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 50 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 |  | CANTEEN BUILDING HVAC DB | KITCHEN-VENTILATION FAN | CANTEEN BUILDING |  | POWER | 0.25 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.44688 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.054516 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 50 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 |  | CANTEEN BUILDING HVAC DB | POT WASH-VENTILATION FAN |  |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.28558 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 50 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 |  | CANTEEN BUILDING HVAC DB | WASH AREA-VENTILATION FAN |  |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 30 | 0 | 10 | 5 | 5 | 50 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.28558 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 50 |  | 2 |  | 15 | 15 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 1420-ACDB-4-0206 | PDB-2 | CANTEEN BUILDING HVAC DB-206 INCOMER |  |  | INCOMER | 29.6947 | kW | 3Ph | 400 | 0.95 | 0.85 | 53.0798 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | OCCUPATIONAL HEALTH CENTER HVAC DB | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | DOCTOR ROOM - SPLIT AC |  |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.50372 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | FIRST AID ROOM - SPLIT AC |  |  | POWER | 1.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 2.6813 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.21588 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | LAB AREA - SPLIT AC |  |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.50372 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | PATIENT WARD - SPLIT AC |  |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.50372 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | WAITING AREA - SPLIT AC 1 |  |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.50372 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | WAITING AREA - SPLIT AC 2 |  |  | POWER | 3.5 | kW | 3Ph | 400 | 0.95 | 0.85 | 6.2563 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.50372 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | GENTS TOILET - VENTILATION |  |  | POWER | 0.25 | kW | 3Ph | 400 | 0.95 | 0.85 | 0.44688 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.03598 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | LADIES TOILET - VENTILATION |  |  | POWER | 0.25 | kW | 1Ph | 230 | 0.95 | 0.85 | 1.3461 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 15 | 0 | 10 | 5 | 3 | 33 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.18849 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 33 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 |  | OCCUPATIONAL HEALTH CENTER HVAC DB | WAITING AREA 2 - SPLIT AC 1 | OCCUPATIONAL HEALTH CENTER |  | POWER | 1.5 | kW | 3Ph | 400 | 0.75 | 0.853 | 3.3843 | 0 | 0.00 | 65 | 0 | 0 | TRENCH | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 12 | 83 | 20 | 8 | 13 | 136 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.8944 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 136 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 1420-ACDB-4-0207 | PDB-2 | OCCUPATIONAL HEALTH CENTER HVAC DB -207 INCOMER |  |  | INCOMER | 25.9474 | kW | 3Ph | 400 | 0.95 | 0.85 | 46.3813 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[33 empty] | 25623.2 | [15 empty] | 25745.8 |  | 460 | [73 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 2270 | 439 | 439 | 423 | 198 | 198 | 2270 | 2249 | 1233 | 1016 | 240 | 993 | 112 | 487 | 394 | 137 | 257 | 145 | 112 | 103 | 16
[124 empty] | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032 | 0 | 4.54 | 0.878 | 0.878 | 0.846 | 0.396 | 0.396 | 4.54 | 4.498 | 2.466 | 2.032 | 0.48 | 1.986 | 0.224 | 0.974 | 0.788 | 0.274 | 0.514 | 0.29 | 0.224 | 0.206 | 0.032
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 3 | 3 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[124 empty] | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0256 | 0 | 3.632 | 0.7024 | 0.7024 | 0.6768 | 0.3168 | 0.3168 | 3.632 | 3.5984 | 1.9728 | 1.6256 | 0.384 | 1.5888 | 0.1792 | 0.7792 | 0.6304 | 0.2192 | 0.4112 | 0.232 | 0.1792 | 0.1648 | 0.0256
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[36 empty] | 1396 |  | 2792
[36 empty] | 37 |  | 111 | [85 empty] | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021333 | 0 | 3.0267 | 0.58533 | 0.58533 | 0.564 | 0.264 | 0.264 | 3.0267 | 2.9987 | 1.644 | 1.3547 | 0.32 | 1.324 | 0.14933 | 0.64933 | 0.52533 | 0.18267 | 0.34267 | 0.19333 | 0.14933 | 0.13733 | 0.021333
[36 empty] | 37 | [88 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 1 | 1 | 1 | 1 | 4 | 3 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## LV Cable sizing_SS-3
LV POWER CABLE SIZING
Sl. No |  |  | LOAD | [12 empty] | SHORT CIRCUIT CURRENT WITHSTAND CAPABILITY |  |  | CABLE DATA | [14 empty] | DERATING FACTOR | [5 empty] | CURRENT CARRYING CAPACITY |  |  | RUNNING CONDITION VOLTAGE DROP |  | MOTOR STARTING VOLTAGE DROP |  | Selected Cable Size
| Tag No. | From | Description | Equipment Location | Bus | Type of feeder | Rated power | UNIT (kW / kVA) | 3Phase / 1Phase | Rated Voltage (V) | Power factor | Efficiency | Rated full load current | Motor starting current | Motor starting power factor | Short circuit current of switchboard (kA) | Short circuit current withstand duration (sec) | Minimum size required for Short circuit withstand capacity (Sq.mm) | Installation | No. of Cores | Size in (Sq.mm) | Cable size | Cable size With (PE) Core | Cable Voltage (kV) | Current Rating of the Cable (A) | Cable resistance at 90°C (Ohm / Ph / km) | Cable reactance at 50Hz (Ohm / Ph / km) | Cable Length with in Electrical Building (m) | Cable Length from Electrical Building to Equipment (m) | Cable length Riser & Dropper (m) | Cable length both side dropping & Termination (m) | Spare 10% | Cable length for each run (m) | Ambient temperature (K1) | Grouping factor (K2) | Ground temperature (K3) | Depth of laying (K4) | Thermal resistivity of ground (K5) | Overall derating factor | Derated current carrying capacity (A) | No. of Runs | Derated current > Rated current | % VOLTAGE DROP DURING RUNNING CONDITION | % VOLTaGE DROP WITHIN PERMISSIBLE LIMIT (YES/NO) | % VOLTAGE DROP DURING STaRTING CONDITION | % VOLTaGE DROP WITHIN PERMISSIBLE LIMIT DURING STaRTING CONDITION (YES/NO) | Selected cable size | Remarks | Total Cable Length in meters | Remarks | No. of End Termination | Cable Route(Sections) | Dia of the conductor(mm) | Total Dia of the conductor(mm) | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | I.A | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | TA | T1.A | U |  | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | H | H1 | I | I1 | I2 | I.A | J | K | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | M | M1 | N | N1 | N2 | O | O1 | P | Q | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | R | R1 | R2 | R1.A | R2.A | S | S.A | S.B | S1 | S1.A | T | T1 | TA | T1.A | U
AMMONIA STORAGE SUBSTATION
PMCC-3
X | 1402-AN001A 1402-AN001B | PMCC-3 | EXHUAST FAN FOR AMMONIA TANK HOLDING COMPRESSOR NOISE HOOD | AMMONIA STORAGE AREA |  | MOTOR | 20 | kW | 3Ph | 400 | 0.82 | 0.933 | 37.7335 | 226.4008 | 0.2 | 65 | 0 | 0 | AIR | 3C | 35 | 3C X 35 | 3C X 35+PE | 0.6/1.0 | 117 | 1.11 | 0.0794 | 18 | 68 | 10 | 10 | 11 | 117 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 1.8269 | YES | 10.9613 | YES | 1R x 0.6/1kV x 3C x 35 Sqmm | 1R x 0.6/1kV x 3C x 35+PE Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1402-B003A | PMCC-3 | HEATER FOR OIL SEPARATOR(1402-PK003B) (230V) | AMMONIA STORAGE AREA |  | POWER | 2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.1621 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.1536 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 134 |  | 2 | I2J | 16 | 16 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1402-B003B | PMCC-3 | HEATER FOR OIL SEPARATOR(1402-PK003B) (230V) | AMMONIA STORAGE AREA |  | POWER | 2 | kW | 3Ph | 400 | 0.8 | 0.867 | 4.1621 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.1536 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 134 |  | 2 | I2J | 16 | 16 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1402-P003A | PMCC-3 | LUBE OIL PUMP FOR (1402-PK003A) | AMMONIA STORAGE AREA |  | MOTOR | 7.5 | kW | 3Ph | 400 | 0.82 | 0.933 | 14.15 | 84.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.695 | YES | 4.3172 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 134 |  | 2 | I2J | 16 | 16 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1402-P003B | PMCC-3 | LUBE OIL PUMP FOR (1402-PK003B) | AMMONIA STORAGE AREA |  | MOTOR | 7.5 | kW | 3Ph | 400 | 0.82 | 0.933 | 14.15 | 84.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.695 | YES | 4.3172 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 134 |  | 2 | I2J | 16 | 16 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1402-P004A | PMCC-3 | LUBE OIL PUMP FOR (1402-PK003A) | AMMONIA STORAGE AREA |  | MOTOR | 7.5 | kW | 3Ph | 400 | 0.82 | 0.933 | 14.15 | 84.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.695 | YES | 4.3172 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 134 |  | 2 | I2J | 16 | 16 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1402-P004B | PMCC-3 | LUBE OIL PUMP FOR (1402-PK003B) | AMMONIA STORAGE AREA |  | MOTOR | 7.5 | kW | 3Ph | 400 | 0.82 | 0.933 | 14.15 | 84.9003 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 2.695 | YES | 4.3172 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 134 |  | 2 | I2J | 16 | 16 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1402-B002A | PMCC-3 | HEATER FOR OIL SEPARATOR(1402-PK003A) (230V) | AMMONIA STORAGE AREA |  | POWER | 2 | kW | 1Ph | 230 | 0.82 | 0.933 | 11.366 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3483 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 134 |  | 2 | I2J | 19 | 19 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1402-B002B | PMCC-3 | HEATER FOR OIL SEPARATOR(1402-PK003A) (230V) | AMMONIA STORAGE AREA |  | POWER | 2 | kW | 1Ph | 230 | 0.82 | 0.933 | 11.366 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 16 | 3C X 16 | 3C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 2.3483 | YES | NA | NA | 1R x 0.6/1kV x 3C x 16 Sqmm | 1R x 0.6/1kV x 3C x 16 Sqmm | 134 |  | 2 | I2J | 19 | 19 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 |  | PMCC-4 | SPACE HEATER OF COMPRESSOR(1402-PK003A) | AMMONIA STORAGE AREA |  | POWER | 0.6 | kW | 1Ph | 230 | 0.82 | 0.933 | 3.4098 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.6833 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 134 |  | 2 | I2J | 15 | 15 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 |  | PMCC-5 | SPACE HEATER OF COMPRESSOR (1402-PK003B) | AMMONIA STORAGE AREA |  | POWER | 0.6 | kW | 1Ph | 230 | 0.82 | 0.933 | 3.4098 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.6833 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | 134 |  | 2 | I2J | 15 | 15 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 |  | PMCC-3 | OIL PUMP FOR OIL CHARGING TROLLEY | AMMONIA STORAGE AREA |  | MOTOR | 1.5 | kW | 3Ph | 400 | 0.82 | 0.933 | 2.83 | 16.9801 | 0.2 | 65 | 0 | 0 | AIR | 3C | 6 | 3C X 6 | 3C X 6+PE | 0.6/1.0 | 51 | 3.94 | 0.0902 | 18 | 83 | 10 | 10 | 13 | 134 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 0.539 | YES | 0.86345 | YES | 1R x 0.6/1kV x 3C x 6 Sqmm | 1R x 0.6/1kV x 3C x 6+PE Sqmm | 134 |  | 2 | I2J | 16 | 16 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other Load | [10 empty] | 0 | [17 empty] | 0 | [92 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1402-B001 | PMCC-3 | ELECTRIC HEATER | AMMONIA STORAGE AREA |  | POWER | 900 | kW | 3Ph | 400 | 0.85 | 0.95 | 1608.7631 | 0 | 0.00 | 65 | 0 | 0 | AIR | 1C | 630 | 1C X 630 | 1C X 630 | 0.6/1.0 | 822 | 0.06 | 0.0843 | 10 | 61 | 10 | 10 | 10 | 101 | 0.89 | 0.81 | NA | NA | NA | 0.7209 | 592.5798 | 3 | YES | 2.2376 | YES | NA | NA | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 3R x 0.6/1.0kV x 1C x 630 Sqmm/Phase | 1212 |  | 18 | I2J | 42 | 126 | [23 empty] | 1 |  | 1 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 1402-MLDB-4-0003 | PMCC-3 | OUTGOING FEEDER FOR MAIN LIGHTING DB-3 / FEEDER | NH3 STORAGE SUBSTATION |  | POWER | 12.75 | kW | 3Ph | 400 | 0.85 | 0.95 | 22.7908 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 16 | 0 | 0 | 0 | 2 | 18 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.37605 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 18 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 1402-WDB-4-0003 | PMCC-3 | OUTGOING FEEDER FOR WELDING & RECEPTACLE DB-3 / FEEDER | NH3 STORAGE SUBSTATION |  | POWER | 87.3 | kW | 3Ph | 400 | 0.85 | 0.95 | 156.05 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 50 | 3.5C X 50 | 3.5C X 50 | 0.6/1.0 | 141 | 0.82 | 0.0792 | 17 | 0 | 0 | 0 | 2 | 19 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 82.8234 | 2 | YES | 0.47421 | YES | NA | NA | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 2R x 0.6/1kV x 3.5C x 50 Sqmm | 38 |  | 4 |  | 30 | 60 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 1402-PDB-4-0003 | PMCC-3 | OUTGOING FEEDER FOR PDB-3 / FEEDER-1 | NH3 STORAGE SUBSTATION |  | POWER | 32.65 | kW | 3Ph | 400 | 0.85 | 0.95 | 58.3624 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 21 | 0 | 0 | 0 | 3 | 24 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.59762 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 24 |  | 2 |  | 27 | 27 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 1402-PDB-4-0003 | PMCC-3 | OUTGOING FEEDER FOR PDB-3 / FEEDER-2 | NH3 STORAGE SUBSTATION |  | POWER | 32.65 | kW | 3Ph | 400 | 0.85 | 0.95 | 58.3624 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 35 | 3.5C X 35 | 3.5C X 35 | 0.6/1.0 | 117 | 1.11 | 0.0794 | 21 | 0 | 0 | 0 | 3 | 24 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 68.7258 | 1 | YES | 0.59762 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 1R x 0.6/1kV x 3.5C x 35 Sqmm | 24 |  | 2 |  | 27 | 27 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 1402-SWG-4-0003 | PMCC-3 | PMCC-3 (INCOMER-1) | NH3 STORAGE SUBSTATION |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84921 | 0.92778 | 2489.2478 | LV BUSDUCT-400V | [110 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 1402-SWG-4-0003 | PMCC-3 | PMCC-3 (INCOMER-2) | NH3 STORAGE SUBSTATION |  | INCOMER | 1600 | kVA | 3Ph | 400 | 0.84921 | 0.92778 | 2489.2478 | LV BUSDUCT-400V | [110 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | PDB-3 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | HVAC SYSTEM | [28 empty] | 0 | [92 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | - | PDB-3 | CONTROL ROOM-SPLIT AC-1 | NH3 STORAGE SUBSTATION |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.954 | 18.7661 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6623 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 87 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | - | PDB-3 | CONTROL ROOM-SPLIT AC-2 | NH3 STORAGE SUBSTATION |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6693 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 87 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | - | PDB-3 | CONTROL ROOM-SPLIT AC-3 | NH3 STORAGE SUBSTATION |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 18.8451 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6693 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 87 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | - | PDB-3 | CONTROL ROOM-SPLIT AC-4 | NH3 STORAGE SUBSTATION |  | POWER | 3.5 | kW | 1Ph | 230 | 0.85 | 0.954 | 18.7661 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 25 | 3C X 25 | 3C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 1.6623 | YES | NA | NA | 1R x 0.6/1kV x 3C x 25 Sqmm | 1R x 0.6/1kV x 3C x 25 Sqmm | 87 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | - | PDB-3 | SWITCHGEAR ROOM VENTILATION FAN 1 | NH3 STORAGE SUBSTATION |  | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.7154 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 87 |  | 2 |  | 18 | 18 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | - | PDB-3 | SWITCHGEAR ROOM VENTILATION FAN 2 | NH3 STORAGE SUBSTATION |  | POWER | 7.5 | kW | 3Ph | 400 | 0.85 | 0.95 | 13.4064 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 6 | 4C X 6 | 4C X 6 | 0.6/1.0 | 51 | 3.94 | 0.0902 | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 29.9574 | 1 | YES | 1.7154 | YES | NA | NA | 1R x 0.6/1kV x 4C x 6 Sqmm | 1R x 0.6/1kV x 4C x 6 Sqmm | 87 |  | 2 |  | 18 | 18 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PDB-3 | SWITCHGEAR ROOM VENTILATION FAN 3 | NH3 STORAGE SUBSTATION |  | POWER | 0.55 | kW | 1Ph | 230 | 0.85 | 0.95 | 2.9614 | 0 | 0.00 | 65 | 0 | 0 | AIR |  | 4 | X 4 | X 4 | 0.6/1.0 | #N/A | #N/A | #N/A | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A |  | #N/A | #N/A | #N/A | NA | NA | R x 0.6/1kV x x 4 Sqmm | R x 0.6/1kV x x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PDB-3 | CONTROL ROOM-SPLIT AC | NH3 STORAGE SUBSTATION |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR |  | 4 | X 4 | X 4 | 0.6/1.0 | #N/A | #N/A | #N/A | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A |  | #N/A | #N/A | #N/A | NA | NA | R x 0.6/1kV x x 4 Sqmm | R x 0.6/1kV x x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PDB-3 | CONTROL ROOM-SPLIT AC | NH3 STORAGE SUBSTATION |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.954 | 8.0426 | 0 | 0.00 | 65 | 0 | 0 | AIR |  | 4 | X 4 | X 4 | 0.6/1.0 | #N/A | #N/A | #N/A | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A |  | #N/A | #N/A | #N/A | NA | NA | R x 0.6/1kV x x 4 Sqmm | R x 0.6/1kV x x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | - | PDB-3 | Corridor-SPLIT AC | NH3 STORAGE SUBSTATION |  | POWER | 1.5 | kW | 1Ph | 230 | 0.85 | 0.95 | 8.0765 | 0 | 0.00 | 65 | 0 | 0 | AIR |  | 4 | X 4 | X 4 | 0.6/1.0 | #N/A | #N/A | #N/A | 29 | 32 | 10 | 8 | 8 | 87 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | #N/A |  | #N/A | #N/A | #N/A | NA | NA | R x 0.6/1kV x x 4 Sqmm | R x 0.6/1kV x x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other Load | [10 empty] | 0 | [17 empty] | 0 | [92 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 1402-SWG-4-0003 | PDB-3 | AUX POWER SUPPLY - 400V AC SWITCHGEAR (BUS-A) | NH3 STORAGE SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.954 | 8.9001 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 9 | 10 | 8 | 6 | 62 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.2102 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 62 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 1402-SWG-4-0003 | PDB-3 | AUX POWER SUPPLY - 400V AC SWITCHGEAR (BUS-B) | NH3 STORAGE SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 11 | 10 | 8 | 6 | 64 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.2545 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 64 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 1402-SWG-4-0003 | PDB-3 | AUX POWER SUPPLY NSPBD SYSTEM-3A | NH3 STORAGE SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 12 | 10 | 8 | 6 | 65 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.2741 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 65 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 1402-SWG-4-0003 | PDB-3 | AUX POWER SUPPLY NSPBD SYSTEM-3B | NH3 STORAGE SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.95 | 8.9376 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 12 | 10 | 8 | 6 | 65 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 1.2741 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 65 |  | 2 | [73 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 1402-TFD-2-0005 | PDB-3 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-5 | NH3 STORAGE SUBSTATION |  | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 14 | 10 | 8 | 7 | 68 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.79974 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 68 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 1402-TFD-2-0006 | PDB-3 | AUX POWER SUPPLY DISTRIBUTION TRANSFORMER-6 | NH3 STORAGE SUBSTATION |  | POWER | 3 | kW | 3Ph | 400 | 0.85 | 0.95 | 5.3625 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 4 | 4C X 4 | 4C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 | 29 | 14 | 10 | 8 | 7 | 68 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.79974 | YES | NA | NA | 1R x 0.6/1kV x 4C x 4 Sqmm | 1R x 0.6/1kV x 4C x 4 Sqmm | 68 |  | 2 |  | 16 | 16 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 1402-PDB-4-0003 | PDB-3 | PDB-3 (INCOMER 1) | NH3 STORAGE SUBSTATION |  | INCOMER | 17.8105 | kW | 3Ph | 400 | 0.85 | 0.951 | 31.8031 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 1402-PDB-4-0003 | PDB-3 | PDB-3 (INCOMER 2) | NH3 STORAGE SUBSTATION |  | INCOMER | 17.8105 | kW | 3Ph | 400 | 0.85 | 0.951 | 31.8031 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MLDB-3 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | NLP-201 | MLDB-03 | LIGHTING DB-201 | AMMONIA STORAGE SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 13 | 0 | 6 | 10 | 3 | 32 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.26189 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 32 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | NLP-202 | MLDB-03 | LIGHTING DB-202 | AMMONIA STORAGE - COMPRESSOR AREA - SLDB (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 4 | 48 | 6 | 10 | 7 | 75 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.61381 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 75 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | NLP-203 | MLDB-03 | LIGHTING DB-203 | AMMONIA STORAGE - PUMP AREA - SLDB (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 4 | 79 | 6 | 10 | 10 | 109 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.89207 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 109 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | NLP-204 | MLDB-03 / NLP-201 | LIGHTING & POWER DB-203 | SECURITY ROOM-2 |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 4 | 79 | 6 | 10 | 10 | 109 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.4302 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 109 |  | 2 |  | 20 | 20 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 1402-MLDB-4-0003 |  | MAIN LIGHTING DB-003 (INCOMER) | AMMONIA STORAGE SUBSTATION |  | INCOMER | 42.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 100 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EMLDB-3 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | ELP-201 | EMLDB-03 | EMERGENCY LIGHTING DB-201 | AMMONIA STORAGE SUBSTATION |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 11 | 0 | 6 | 10 | 3 | 30 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 0.39362 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | ELP-202 | EMLDB-03 | EMERGENCY LIGHTING DB-202 | AMMONIA STORAGE AREA (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 8 | 48 | 6 | 10 | 8 | 80 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.0497 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 80 |  | 2 |  | 20 | 20 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | ELP-203 | EMLDB-03 | EMERGENCY LIGHTING DB-203 | AMMONIA STORAGE AREA (VENDOR PACKAGE) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 10 | 4C X 10 | 4C X 10 | 0.6/1.0 | 60 | 3.94 | 0.0852 | 8 | 79 | 6 | 10 | 11 | 114 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 35.244 | 1 | YES | 1.4958 | YES | NA | NA | 1R x 0.6/1kV x 4C x 10 Sqmm | 1R x 0.6/1kV x 4C x 10 Sqmm | 114 |  | 2 |  | 20 | 20 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 1421-EMLDB-4-0001 |  | EMERGENCY MAIN LIGHTING DB-001 (INCOMER) | AMMONIA STORAGE SUBSTATION |  | INCOMER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 63 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WDB-3 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | WSDB-201 | WDB-03 | POWER RECEPTACLE DB-201 | AMMONIA STORAGE SUBSTATION |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 7 | 0 | 6 | 10 | 3 | 26 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.27179 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 26 |  | 2 |  | 25 | 25 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | WSDB-202 | WDB-03 | WELDING RECEPTACLE DB-202 | AMMONIA STORAGE (COMPRESSOR AREA) |  | POWER | 10 | kW | 3Ph | 400 | 0.85 | 0.951 | 17.8563 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3.5C | 25 | 3.5C X 25 | 3.5C X 25 | 0.6/1.0 | 95 | 1.54 | 0.0816 | 10 | 0 | 6 | 10 | 3 | 29 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 55.803 | 1 | YES | 0.30315 | YES | NA | NA | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 1R x 0.6/1kV x 3.5C x 25 Sqmm | 29 |  | 2 |  | 25 | 25 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | WS-201 & 202 | WDB-03 | WELDING SOCKET -201 & 202 | AMMONIA STORAGE SUBSTATION & AMMONIA STORAGE (COMPRESSOR AREA) |  | POWER | 5 | kW | 3Ph | 400 | 0.85 | 0.951 | 8.9282 | 0 | 0.00 | 65 | 0 | 0 | AIR | 4C | 16 | 4C X 16 | 4C X 16 | 0.6/1.0 | 70 | 2.44 | 0.0815 | 10 | 0 | 6 | 10 | 3 | 29 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 41.118 | 1 | YES | 0.23734 | YES | NA | NA | 1R x 0.6/1kV x 4C x 16 Sqmm | 1R x 0.6/1kV x 4C x 16 Sqmm | 29 |  | 2 |  | 21 | 21 | [70 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 1402-WDB-4-0003 |  | WELDING & RECEPTACLE DB-003 (INCOMER) | AMMONIA STORAGE SUBSTATION |  | INCOMER | 42.5 | kW | 3Ph | 400 | 0.85 | 0.951 | 125 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | AC UPS SUB DB-4 | [121 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-1 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-2 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-3 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-4 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-5 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-6 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-7 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-8 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-9 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-10 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-11 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-12 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-13 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-14 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-15 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-16 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-17 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-18 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-19 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-20 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-21 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-22 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-23 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-24 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-25 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-26 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-27 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-28 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-29 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X |  |  | FEEDER-30 | Ammonia Storage & BOG Compressor |  | POWER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | 0 | 0.00 | 65 | 0 | 0 | AIR | 3C | 4 | 3C X 4 | 3C X 4 | 0.6/1.0 | 38 | 5.9 | 0.0947 |  |  | 10 | 8 | 2 | 20 | 0.89 | 0.66 | NA | NA | NA | 0.5874 | 22.3212 | 1 | YES | 0.4577 | YES | NA | NA | 1R x 0.6/1kV x 3C x 4 Sqmm | 1R x 0.6/1kV x 3C x 4 Sqmm | [76 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1402-UPS-SDB-4-0004 |  | AC UPS SUB DB-4_INCOMER-1 | Ammonia Storage & BOG Compressor |  | INCOMER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
X | 1402-UPS-SDB-4-0004 |  | AC UPS SUB DB-4_INCOMER-2 | Ammonia Storage & BOG Compressor |  | INCOMER |  | kW | 1Ph | 230 | 0.85 | 0.95 | 6 | [111 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[49 empty] | 4307 |  | 92 | [73 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.612 | 0 | 0.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4896 | 0 | 0.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[124 empty] | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.408 | 0 | 0.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[125 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sheet1 (hidden)
Cable Tray Sections | Tray Size | UOM | A1 | A | B | B1 | C | D | D1 | D2 | D3 | E | E0 | E1 | E2 | E3 | E4 | E5 | E6 | F | G | G1 | G2 | G3 | G4 | H | I | J | J1 | J2 | J3 | K | L | L1 | L2 | L3 | L4 | M | N | O | O1 | P | Q | Q1 | Q2 | Q3 | R | R1 | R2 | S | T
Instrumentation Cable Trays
IS Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos
Non IS Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos
F&G Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos
FOC & Telecom Cable Tray | Total Cable Dia
| 600 | Nos
| 450 | Nos
| 300 | Nos

## Summary
MV & LV Cable BOQ Summary
Sl. No. |  |  | Cable size | Cable Voltage (kV) | Conductor Type | Insulation | Armoured / Unarmoured | [8 empty] | Total Cable Length (Meter) | Remarks | [8 empty] | No. of End Termination | No. of End Termination with 5% | Total No. of End Termination | Remarks
[8 empty] | 33kV | 11kV | LV-SS-1 | LV-SS-2 | LV-SS-3 | LV-SS-4 | LV-SWI | LV-SS-5 |  |  | 33kV | 11kV | LV-SS-1 | LV-SS-2 | LV-SS-3 | LV-SS-4 | LV-SWI | LV-SS-5
For LV Cables - 0.6/1kV CU. or Al. XLPE Armoured
1 | 3C X 1.5 |  | 3C X 1.5 | 0.6/1.0 | COPPER | XLPE | Armoured |  | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
2 | 3C X 2.5 |  | 3C X 2.5 | 0.6/1.0 | COPPER | XLPE | Armoured |  | 1440 | 6267 | 2920.8 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | 16 | 38 | 34 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 10113.8
3 | 3C X 4 |  | 3C X 4 | 0.6/1.0 | COPPER | XLPE | Armoured |  | 5140 | 4345 | 1184 | 268 | #REF! | #REF! | #REF! | #REF! |  |  | 22 | 42 | 42 | 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 14044
4 | 3C X 6 |  | 3C X 6 | 0.6/1.0 | COPPER | XLPE | Armoured |  | 3210 | 868 | 69 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | 6 | 8 | 2 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2441
5 | 3C X 10 |  | 3C X 10 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 110
6 | 3C X 16 |  | 3C X 16 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 4132 | 2050 | 268 | #REF! | #REF! | #REF! | #REF! |  |  |  | 84 | 70 | 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 3228
7 | 3C X 25 |  | 3C X 25 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 4515 | 0 | 348 | #REF! | #REF! | #REF! | #REF! |  |  |  | 38 | 0 | 8 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 3439
8 | 3C X 35 |  | 3C X 35 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | 0 | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
9 | 3C X 50 |  | 3C X 50 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 1594 | 591.6 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 24 | 8 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 3135.6
10 | 3C X 70 |  | 3C X 70 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 461 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 2 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 461
11 | 3C X 95 |  | 3C X 95 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 646 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 2 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 646
12 | 3C X 120 |  | 3C X 120 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 780
13 | 3C X 150 |  | 3C X 150 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 692
14 | 3C X 185 |  | 3C X 185 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
15 | 3C X 240 |  | 3C X 240 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
16 | 3C X 300 |  | 3C X 300 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
17 | 3C X 400 |  | 3C X 400 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
18 | 3C X 1.5 | +PE | 3C X 1.5+PE | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
19 | 3C X 2.5 | +PE | 3C X 2.5+PE | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
20 | 3C X 4 | +PE | 3C X 4+PE | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 6758 | 1511.8 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 36 | 34 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 16531.3
21 | 3C X 6 | +PE | 3C X 6+PE | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 939 | 171 | 670 | #REF! | #REF! | #REF! | #REF! |  |  |  | 6 | 2 | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 1997.4
22 | 3C X 10 | +PE | 3C X 10+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
23 | 3C X 16 | +PE | 3C X 16+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 1490 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 8 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2666
24 | 3C X 25 | +PE | 3C X 25+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 3781 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 28 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 4730
25 | 3C X 35 | +PE | 3C X 35+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 2308 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 12 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2275.6
26 | 3C X 50 | +PE | 3C X 50+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 451 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 6 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 589
27 | 3C X 70 | +PE | 3C X 70+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 2864 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 24 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 1216
28 | 3C X 95 | +PE | 3C X 95+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 5092.5 | 900.8 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 24 | 12 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 5243.3
29 | 3C X 120 | +PE | 3C X 120+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 1560.5
30 | 3C X 150 | +PE | 3C X 150+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 1488 | 588 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 8 | 6 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 1488
31 | 3C X 185 | +PE | 3C X 185+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 1288 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 16 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 1288
32 | 3C X 240 | +PE | 3C X 240+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 1284 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 12 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 828
33 | 3C X 300 | +PE | 3C X 300+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 1426 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 12 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 1898
34 | 3C X 400 | +PE | 3C X 400+PE | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
35 | 3.5C X 25 |  | 3.5C X 25 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 3298 | 2452 | 55 | #REF! | #REF! | #REF! | #REF! |  |  |  | 36 | 26 | 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 5733
36 | 3.5C X 35 |  | 3.5C X 35 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 6541 | 2646 | 48 | #REF! | #REF! | #REF! | #REF! |  |  |  | 44 | 28 | 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 10756
37 | 3.5C X 50 |  | 3.5C X 50 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 3453 | 260 | 38 | #REF! | #REF! | #REF! | #REF! |  |  |  | 18 | 2 | 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2162
38 | 3.5C X 70 |  | 3.5C X 70 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 2046 | 234 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 12 | 6 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2793
39 | 3.5C X 95 |  | 3.5C X 95 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 2535 | 663 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 16 | 8 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 3059
40 | 3.5C X 120 |  | 3.5C X 120 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 197 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 2 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 174
41 | 3.5C X 150 |  | 3.5C X 150 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 1835 | 84.4 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 42 | 2 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 1822
42 | 3.5C X 185 |  | 3.5C X 185 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 710
43 | 3.5C X 240 |  | 3.5C X 240 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
44 | 3.5C X 300 |  | 3.5C X 300 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 1786 | 130 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 8 | 8 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 6826
45 | 3.5C X 400 |  | 3.5C X 400 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
46 | 4C X 1.5 |  | 4C X 1.5 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
47 | 4C X 2.5 |  | 4C X 2.5 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
48 | 4C X 4 |  | 4C X 4 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 5133 | 2842.4 | 660 | #REF! | #REF! | #REF! | #REF! |  |  |  | 64 | 94 | 16 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 10992
49 | 4C X 6 |  | 4C X 6 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 2203 | 0 | 174 | #REF! | #REF! | #REF! | #REF! |  |  |  | 28 | 0 | 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2604
50 | 4C X 10 |  | 4C X 10 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 334 | 740 | 303 | #REF! | #REF! | #REF! | #REF! |  |  |  | 8 | 12 | 6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 2244
51 | 4C X 16 |  | 4C X 16 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 1147 | 2487 | 263 | #REF! | #REF! | #REF! | #REF! |  |  |  | 12 | 28 | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 4320
52 | 4C X 25 |  | 4C X 25 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | #N/A | 0 | 0 | #REF! | #REF! | #REF! | #N/A |  |  |  | #N/A | 0 | 0 | #REF! |  | #REF! | #N/A | #N/A | #N/A |  | 0
53 | 4C X 35 |  | 4C X 35 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
54 | 4C X 50 |  | 4C X 50 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
55 | 4C X 70 |  | 4C X 70 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
56 | 4C X 95 |  | 4C X 95 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
57 | 4C X 120 |  | 4C X 120 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
58 | 4C X 150 |  | 4C X 150 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
59 | 4C X 185 |  | 4C X 185 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
60 | 4C X 240 |  | 4C X 240 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
61 | 4C X 300 |  | 4C X 300 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
62 | 4C X 400 |  | 4C X 400 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
63 | 5C X 1.5 |  | 5C X 1.5 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
64 | 5C X 2.5 |  | 5C X 2.5 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
65 | 5C X 4 |  | 5C X 4 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
66 | 5C X 6 |  | 5C X 6 | 0.6/1.0 | COPPER | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
67 | 5C X 10 |  | 5C X 10 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
68 | 5C X 16 |  | 5C X 16 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
69 | 5C X 25 |  | 5C X 25 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
70 | 5C X 35 |  | 5C X 35 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
71 | 5C X 50 |  | 5C X 50 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
72 | 5C X 70 |  | 5C X 70 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
73 | 1C X 185 |  | 1C X 185 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
74 | 1C X 240 |  | 1C X 240 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
75 | 1C X 300 |  | 1C X 300 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0
76 | 1C X 400 |  | 1C X 400 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 0 | 0 | 0 | #REF! |  | #REF! | #REF! | #REF! | #REF! |  | 0
77 | 1C X 500 |  | 1C X 500 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 656 | 0 | 0 | #REF! | #REF! | #REF! | #REF! |  |  |  | 24 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 656
78 | 1C X 630 |  | 1C X 630 | 0.6/1.0 | ALUMINIUM | XLPE | Armoured |  |  | 2770 | 0 | 1212 | #REF! | #REF! | #REF! | #REF! |  |  |  | 130 | 0 | 18 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 3982
0
For MV Cables - 6/10 (12) kV CU. or Al. XLPE Armoured
1 | 1C X 70 |  | 1C X 70 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
2 | 1C X 95 |  | 1C X 95 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
3 | 1C X 120 |  | 1C X 120 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
4 | 1C X 150 |  | 1C X 150 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
5 | 1C X 185 |  | 1C X 185 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
6 | 1C X 240 |  | 1C X 240 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
7 | 1C X 300 |  | 1C X 300 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
8 | 1C X 400 |  | 1C X 400 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 100 | [6 empty] | 100 |  |  | 4 | [6 empty] | 4 | 1 | 5 |  | 138
9 | 1C X 500 |  | 1C X 500 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
10 | 1C X 630 |  | 1C X 630 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
11 | 1C X 800 |  | 1C X 800 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
12 | 1C X 1000 |  | 1C X 1000 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
13 | 3C X 70 |  | 3C X 70 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
14 | 3C X 95 |  | 3C X 95 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
15 | 3C X 120 |  | 3C X 120 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
16 | 3C X 150 |  | 3C X 150 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 14150 | [6 empty] | 14150 |  |  | 72 | [6 empty] | 72 | 4 | 76 |  | 14245
17 | 3C X 185 |  | 3C X 185 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 950 | [6 empty] | 950 |  |  | 8 | [6 empty] | 8 | 1 | 9 |  | 943
18 | 3C X 240 |  | 3C X 240 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
19 | 3C X 300 |  | 3C X 300 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
20 | 3C X 400 |  | 3C X 400 | 3.8/6.6 | ALUMINIUM | XLPE | Armoured |  | 0 | [6 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
[16 empty] | 0 |  |  | 0 | [6 empty] | 0 | 0 | 0 |  | 0
For MV Cables - 18/30(36) kV CU. or Al. XLPE Armoured
1 | 1C X 95 |  | 1C X 95 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
2 | 1C X 120 |  | 1C X 120 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
3 | 1C X 150 |  | 1C X 150 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
4 | 1C X 185 |  | 1C X 185 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
5 | 1C X 240 |  | 1C X 240 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 756
6 | 1C X 300 |  | 1C X 300 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
7 | 1C X 400 |  | 1C X 400 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
8 | 1C X 500 |  | 1C X 500 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
9 | 1C X 630 |  | 1C X 630 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
10 | 1C X 800 |  | 1C X 800 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
11 | 1C X 1000 |  | 1C X 1000 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
12 | 3C X 95 |  | 3C X 95 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
13 | 3C X 120 |  | 3C X 120 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
14 | 3C X 150 |  | 3C X 150 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 1227
15 | 3C X 185 |  | 3C X 185 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
16 | 3C X 240 |  | 3C X 240 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 6150
17 | 3C X 300 |  | 3C X 300 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
18 | 3C X 400 |  | 3C X 400 | 18/30 | ALUMINIUM | XLPE | Armoured | #REF! | [7 empty] | #REF! |  | #REF! | [7 empty] | #REF! | #REF! | #REF! |  | 0
[8 empty] | #REF! | 24990 | #N/A | 25745.8 | 4307 | #REF! | #REF! | #REF! |  |  | #REF! | 128 | #N/A | 460 | 92 | #REF! | #REF! | #REF!

## Tray-S_old (hidden)
sl No. | Section | Toute | Equipments | feeder no. | no. of runs each feeder | size | dia of each cable | Total no. of runs | total dia require | Tray Size | Total Treay requirement | no of Trays
1 | K-K | towards Electrolyser | 33kV Electrolyzer rectifier Trafo | 32 | 1 | 3C x 150 Sqmm | 86 | 32 | 2752 | 600 | 4.5867 | 5
1 | A-A | towards CT & OTHER SS | 11KV T/F & Motor | 25 | 1 | 3C x 95 Sqmm | 55 | 25 | 1375 | 600 | 2.2917 | 3
1 | B-B | towards NH3 & OTHER SS | 11KV T/F & Motor | 17 | 1 | 3C x 95 Sqmm | 55 | 17 | 935 | 600 | 1.5583 | 2
[5 empty] | 3 | 2
|  |  |  | 14 |  |  | 8+(8+3)
3750
|  | 2300 |  |  | 3 | 13
1450
[7 empty] | B | C
[7 empty] | 19 | 15
5.6